LEBT Vacuum Control System - Verification and Validation Plan

|  | Name | Role/Title |
| --- | --- | --- |
| Owner | François Bellorini | Control System Engineer |
| Reviewer | Hilko Spoelstra | Vacuum Engineer |
| Reviewer | Simone Scolari | Vacuum Engineer |
| Reviewer | Hector Novella | Deputy Project Manager |
| Reviewer | Henrik Carling | ICS Division - Head of Hardware & Integration Group |
| Approver | Marcelo Juni Ferreira | Vacuum Group Leader |
| Approver | Timo Korhonen | ICS Division - Chief Engineer |

| Table of content | Page |
| --- | --- |

1.	Introduction	18

2.	Issuing organisation	18

3.	System characteristics	18

3.1.	System purpose	18

3.2.	System overview	18

3.3.	Notation for description	18

4.	Verification identification	19

4.1.	Support Environment	19

4.2.	Configuration	19

4.3.	Setup	19

5.	Test Cases “LEBT-010:VAC-VPSU" (Rack Power Supply)	20

5.1.	Test case LEBT-010:VAC-VPSU-00000	20

5.1.1.	Support Environment.	20

5.1.2.	Configuration	20

5.1.3.	Setup	20

5.1.4.	Primary pump & Primary Pump Controller Verification: Procedure	20

5.1.4.1.	LEBT-010:VAC-VPSU-00010: List of requirements	21

5.1.4.2.	LEBT-010:VAC-VPSU-00000: Procedure of verification	22

6.	Test Cases “ISRC-010:VAC" (Ion Source)	24

6.1.	Test case ISRC-010:VAC-VPM-00011	24

6.1.1.	Pressure Manometer Verification: Support Environment.	24

6.1.2.	Pressure Manometer Verification: Configuration	24

6.1.3.	Pressure Manometer Verification: Setup	24

6.1.4.	Pressure Manometer Verification: Procedure	24

6.1.4.1.	ISRC-010:VAC-VPM-00011: List of requirements	25

6.1.4.2.	ISRC-010:VAC-VPM-00011: Procedure of verification	26

6.2.	Test case ISRC-010:VAC-VVA-01100	28

6.2.1.	Angle Valves & Gates Valves Verification: Support Environment.	28

6.2.2.	Angle Valves & Gates Valves Verification: Configuration	28

6.2.3.	Angle Valves & Gates Valves Verification: Setup	28

6.2.4.	Angle Valves & Gates Valves Verification: Procedure	28

6.2.4.1.	ISRC-010:VAC-VVA-01100: List of requirements	29

6.2.4.2.	ISRC-010:VAC-VVA-01100: Procedure of verification	29

6.3.	Test case ISRC-010:VAC-VVMC-01100	38

6.3.1.	Mass Flow Meter & Mass Flow Meter Controller Verification: Support Environment.	38

6.3.2.	Mass Flow Meter & Mass Flow Meter Controller Verification: Configuration	38

6.3.3.	Mass Flow Meter & Mass Flow Meter Controller Verification: Setup	38

6.3.4.	Mass Flow Meter & Mass Flow Meter Controller Verification: Procedure	38

6.3.4.1.	ISRC-010:VAC-VVMC-01100: List of requirements	39

6.3.4.2.	ISRC-010:VAC-VVMC-01100: Procedure of verification	40

7.	Test Cases “LEBT-010:VAC" (First Vacuum Sector)	42

7.1.	Test case LEBT-010:VAC-VPDP-00031	42

7.1.1.	Primary Pump & Primary Pump Controller Verification: Support Environment.	42

7.1.2.	Primary Pump & Primary Pump Controller Verification: Configuration	42

7.1.3.	Primary Pump & Primary Pump Controller Verification: Setup	42

7.1.4.	Primary Pump & Primary Pump Controller Verification: Procedure	42

7.1.4.1.	LEBT-010:VAC-VPDP-00031: List of requirements	43

7.1.4.2.	LEBT-010:VAC-VPDP-00031: Procedure of verification	44

7.2.	Test case LEBT-010:VAC-VVA-00031	50

7.2.1.	Angle Valves & Gates Valves Verification: Support Environment.	50

7.2.2.	Angle Valves & Gates Valves Verification: Configuration	50

7.2.3.	Angle Valves & Gates Valves Verification: Setup	50

7.2.4.	Angle Valves & Gates Valves Verification: Procedure	50

7.2.4.1.	LEBT-010:VAC-VVA-00031: List of requirements	51

7.2.4.2.	LEBT-010:VAC-VVA-00031: Procedure of verification	51

7.3.	Test case LEBT-010:VAC-VGP-00021	58

7.3.1.	Gauge & Gauge Controller Verification: Support Environment.	58

7.3.2.	Gauge & Gauge Controller Verification: Configuration	58

7.3.3.	Gauge & Gauge Controller Verification: Setup	58

7.3.4.	Gauge & Gauge Controller Verification: Procedure	58

7.3.4.1.	LEBT-010:VAC-VGP-00021: List of requirements	59

7.3.4.2.	LEBT-010:VAC-VGP-00021: Procedure of verification	60

7.4.	Test case LEBT-010:VAC-VPT-02100	62

7.4.1.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Support Environment.	62

7.4.2.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Configuration	62

7.4.3.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Setup	62

7.4.4.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Procedure	62

7.4.4.1.	LEBT-010:VAC-VPT-02100: List of requirements	63

7.4.4.2.	LEBT-010:VAC-VPT-02100: Procedure of verification	64

7.5.	Test case LEBT-010:VAC-VVA-02100	68

7.5.1.	Angle Valves & Gates Valves Verification: Support Environment.	68

7.5.2.	Angle Valves & Gates Valves Verification: Configuration	68

7.5.3.	Angle Valves & Gates Valves Verification: Setup	68

7.5.4.	Angle Valves & Gates Valves Verification: Procedure	68

7.5.4.1.	LEBT-010:VAC-VVA-02100: List of requirements	69

7.5.4.2.	LEBT-010:VAC-VVA-02100: Procedure of verification	69

7.6.	Test case LEBT-010:VAC-VPT-03100	76

7.6.1.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Support Environment.	76

7.6.2.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Configuration	76

7.6.3.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Setup	76

7.6.4.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Procedure	76

7.6.4.1.	LEBT-010:VAC-VPT-03100: List of requirements	77

7.6.4.2.	LEBT-010:VAC-VPT-03100: Procedure of verification	78

7.7.	Test case LEBT-010:VAC-VVA-03100	82

7.7.1.	Angle Valves & Gates Valves Verification: Support Environment.	82

7.7.2.	Angle Valves & Gates Valves Verification: Configuration	82

7.7.3.	Angle Valves & Gates Valves Verification: Setup	82

7.7.4.	Angle Valves & Gates Valves Verification: Procedure	82

7.7.4.1.	LEBT-010:VAC-VVA-03100: List of requirements	83

7.7.4.2.	LEBT-010:VAC-VVA-03100: Procedure of verification	83

7.8.	Test case LEBT-010:VAC-VGP-10000	90

7.8.1.	Gauge & Gauge Controller Verification: Support Environment.	90

7.8.2.	Gauge & Gauge Controller Verification: Configuration	90

7.8.3.	Gauge & Gauge Controller Verification: Setup	90

7.8.4.	Gauge & Gauge Controller Verification: Procedure	90

7.8.4.1.	LEBT-010:VAC-VGP-10000: List of requirements	91

7.8.4.2.	LEBT-010:VAC-VGP-10000: Procedure of verification	92

7.9.	Test case LEBT-010:VAC-VGC-10000	94

7.9.1.	Gauge & Gauge Controller Verification: Support Environment.	94

7.9.2.	Gauge & Gauge Controller Verification: Configuration	94

7.9.3.	Gauge & Gauge Controller Verification: Setup	94

7.9.4.	Gauge & Gauge Controller Verification: Procedure	94

7.9.4.1.	LEBT-010:VAC-VGC-10000: List of requirements	95

7.9.4.2.	LEBT-010:VAC-VGC-10000: Procedure of verification	96

7.10.	Test case LEBT-010:VAC-VGD-10000	98

7.10.1.	Gauge & Gauge Controller Verification: Support Environment.	98

7.10.2.	Gauge & Gauge Controller Verification: Configuration	98

7.10.3.	Gauge & Gauge Controller Verification: Setup	98

7.10.4.	Gauge & Gauge Controller Verification: Procedure	98

7.10.4.1.LEBT-010:VAC-VGD-10000: List of requirements	99

7.10.4.2.LEBT-010:VAC-VGD-10000: Procedure of verification	100

7.11.	Test case LEBT-010:VAC-VPG-10001	102

7.11.1.	Vacuum Pumping Group Verification: Support Environment.	102

7.11.2.	Vacuum Pumping Group Verification: Configuration	102

7.11.3.	Vacuum Pumping Group Verification: Setup	102

7.11.4.	Vacuum Pumping Group Verification: Procedure	102

7.11.4.1.LEBT-010:VAC-VPG-10001: List of requirements	103

7.11.4.2.LEBT-010:VAC-VPG-10001: Procedure of verification	104

7.12.	Test case LEBT-010:VAC-VPM-00011	120

7.12.1.	Pressure Manometer Verification: Support Environment.	120

7.12.2.	Pressure Manometer Verification: Configuration	120

7.12.3.	Pressure Manometer Verification: Setup	120

7.12.4.	Pressure Manometer Verification: Procedure	120

7.12.4.1.LEBT-010:VAC-VPM-00011: List of requirements	121

7.12.4.2.LEBT-010:VAC-VPM-00011: Procedure of verification	122

7.13.	Test case LEBT-010:VAC-VVA-01100	124

7.13.1.	Angle Valves & Gates Valves Verification: Support Environment.	124

7.13.2.	Angle Valves & Gates Valves Verification: Configuration	124

7.13.3.	Angle Valves & Gates Valves Verification: Setup	124

7.13.4.	Angle Valves & Gates Valves Verification: Procedure	124

7.13.4.1.LEBT-010:VAC-VVA-01100: List of requirements	125

7.13.4.2.LEBT-010:VAC-VVA-01100: Procedure of verification	125

7.14.	Test case LEBT-010:VAC-VVMC-01100	134

7.14.1.	Mass Flow Meter & Mass Flow Meter Controller Verification: Support Environment.	134

7.14.2.	Mass Flow Meter & Mass Flow Meter Controller Verification: Configuration	134

7.14.3.	Mass Flow Meter & Mass Flow Meter Controller Verification: Setup	134

7.14.4.	Mass Flow Meter & Mass Flow Meter Controller Verification: Procedure	134

7.14.4.1.LEBT-010:VAC-VVMC-01100: List of requirements	135

7.14.4.2.LEBT-010:VAC-VVMC-01100: Procedure of verification	136

7.15.	Test case LEBT-010:VAC-VGR-10000	138

7.15.1.	Residual Gas Analyzer & Residual Gas Analyzer Controller Verification: Support Environment.	138

7.15.2.	Residual Gas Analyzer & Residual Gas Analyzer Controller Verification: Configuration	138

7.15.3.	Residual Gas Analyzer & Residual Gas Analyzer Controller Verification: Setup	138

7.15.4.	Residual Gas Analyzer & Residual Gas Analyzer Controller Verification: Procedure	138

7.15.4.1.LEBT-010:VAC-VGR-10000: List of requirements	139

7.15.4.2.LEBT-010:VAC-VGR-10000: Procedure of verification	140

8.	Test Cases “LEBT-010:VAC" (Second Vacuum Sector)	142

8.1.	Test case LEBT-010:VAC-VPDP-00071	142

8.1.1.	Primary Pump & Primary Pump Controller Verification: Support Environment.	142

8.1.2.	Primary Pump & Primary Pump Controller Verification: Configuration	142

8.1.3.	Primary Pump & Primary Pump Controller Verification: Setup	142

8.1.4.	Primary Pump & Primary Pump Controller Verification: Procedure	142

8.1.4.1.	LEBT-010:VAC-VPDP-00071: List of requirements	143

8.1.4.2.	LEBT-010:VAC-VPDP-00071: Procedure of verification	144

8.2.	Test case LEBT-010:VAC-VVA-00071	150

8.2.1.	Angle Valves & Gates Valves Verification: Support Environment.	150

8.2.2.	Angle Valves & Gates Valves Verification: Configuration	150

8.2.3.	Angle Valves & Gates Valves Verification: Setup	150

8.2.4.	Angle Valves & Gates Valves Verification: Procedure	150

8.2.4.1.	LEBT-010:VAC-VVA-00071: List of requirements	151

8.2.4.2.	LEBT-010:VAC-VVA-00071: Procedure of verification	151

8.3.	Test case LEBT-010:VAC-VGP-00081	158

8.3.1.	Gauge & Gauge Controller Verification: Support Environment.	158

8.3.2.	Gauge & Gauge Controller Verification: Configuration	158

8.3.3.	Gauge & Gauge Controller Verification: Setup	158

8.3.4.	Gauge & Gauge Controller Verification: Procedure	158

8.3.4.1.	LEBT-010:VAC-VGP-00081: List of requirements	159

8.3.4.2.	LEBT-010:VAC-VGP-00081: Procedure of verification	160

8.4.	Test case LEBT-010:VAC-VPT-06100	162

8.4.1.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Support Environment.	162

8.4.2.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Configuration	162

8.4.3.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Setup	162

8.4.4.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Procedure	162

8.4.4.1.	LEBT-010:VAC-VPT-06100: List of requirements	163

8.4.4.2.	LEBT-010:VAC-VPT-06100: Procedure of verification	164

8.5.	Test case LEBT-010:VAC-VVA-06100	168

8.5.1.	Angle Valves & Gates Valves Verification: Support Environment.	168

8.5.2.	Angle Valves & Gates Valves Verification: Configuration	168

8.5.3.	Angle Valves & Gates Valves Verification: Setup	168

8.5.4.	Angle Valves & Gates Valves Verification: Procedure	168

8.5.4.1.	LEBT-010:VAC-VVA-06100: List of requirements	169

8.5.4.2.	LEBT-010:VAC-VVA-06100: Procedure of verification	169

8.6.	Test case LEBT-010:VAC-VPT-07100	176

8.6.1.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Support Environment.	176

8.6.2.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Configuration	176

8.6.3.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Setup	176

8.6.4.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Procedure	176

8.6.4.1.	LEBT-010:VAC-VPT-07100: List of requirements	177

8.6.4.2.	LEBT-010:VAC-VPT-07100: Procedure of verification	178

8.7.	Test case LEBT-010:VAC-VVA-07100	182

8.7.1.	Angle Valves & Gates Valves Verification: Support Environment.	182

8.7.2.	Angle Valves & Gates Valves Verification: Configuration	182

8.7.3.	Angle Valves & Gates Valves Verification: Setup	182

8.7.4.	Angle Valves & Gates Valves Verification: Procedure	182

8.7.4.1.	LEBT-010:VAC-VVA-07100: List of requirements	183

8.7.4.2.	LEBT-010:VAC-VVA-07100: Procedure of verification	183

8.8.	Test case LEBT-010:VAC-VGP-30000	190

8.8.1.	Gauge & Gauge Controller Verification: Support Environment.	190

8.8.2.	Gauge & Gauge Controller Verification: Configuration	190

8.8.3.	Gauge & Gauge Controller Verification: Setup	190

8.8.4.	Gauge & Gauge Controller Verification: Procedure	190

8.8.4.1.	LEBT-010:VAC-VGP-30000: List of requirements	191

8.8.4.2.	LEBT-010:VAC-VGP-30000: Procedure of verification	192

8.9.	Test case LEBT-010:VAC-VGC-30000	194

8.9.1.	Gauge & Gauge Controller Verification: Support Environment.	194

8.9.2.	Gauge & Gauge Controller Verification: Configuration	194

8.9.3.	Gauge & Gauge Controller Verification: Setup	194

8.9.4.	Gauge & Gauge Controller Verification: Procedure	194

8.9.4.1.	LEBT-010:VAC-VGC-30000: List of requirements	195

8.9.4.2.	LEBT-010:VAC-VGC-30000: Procedure of verification	196

8.10.	Test case LEBT-010:VAC-VPT-99998	198

8.10.1.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Support Environment.	198

8.10.2.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Configuration	198

8.10.3.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Setup	198

8.10.4.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Procedure	198

8.10.4.1.LEBT-010:VAC-VPT-99998: List of requirements	199

8.10.4.2.LEBT-010:VAC-VPT-99998: Procedure of verification	200

8.11.	Test case LEBT-010:VAC-VVA-99998	204

8.11.1.	Angle Valves & Gates Valves Verification: Support Environment.	204

8.11.2.	Angle Valves & Gates Valves Verification: Configuration	204

8.11.3.	Angle Valves & Gates Valves Verification: Setup	204

8.11.4.	Angle Valves & Gates Valves Verification: Procedure	204

8.11.4.1.LEBT-010:VAC-VVA-99998: List of requirements	205

8.11.4.2.LEBT-010:VAC-VVA-99998: Procedure of verification	205

8.12.	Test case LEBT-010:VAC-VPT-99999	212

8.12.1.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Support Environment.	212

8.12.2.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Configuration	212

8.12.3.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Setup	212

8.12.4.	Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Procedure	212

8.12.4.1.LEBT-010:VAC-VPT-99999: List of requirements	213

8.12.4.2.LEBT-010:VAC-VPT-99999: Procedure of verification	214

8.13.	Test case LEBT-010:VAC-VVA-99999	218

8.13.1.	Angle Valves & Gates Valves Verification: Support Environment.	218

8.13.2.	Angle Valves & Gates Valves Verification: Configuration	218

8.13.3.	Angle Valves & Gates Valves Verification: Setup	218

8.13.4.	Angle Valves & Gates Valves Verification: Procedure	218

8.13.4.1.LEBT-010:VAC-VVA-99999: List of requirements	219

8.13.4.2.LEBT-010:VAC-VVA-99999: Procedure of verification	219

8.14.	Test case LEBT-010:VAC-VGP-99999	226

8.14.1.	Gauge & Gauge Controller Verification: Support Environment.	226

8.14.2.	Gauge & Gauge Controller Verification: Configuration	226

8.14.3.	Gauge & Gauge Controller Verification: Setup	226

8.14.4.	Gauge & Gauge Controller Verification: Procedure	226

8.14.4.1.LEBT-010:VAC-VGP-99999: List of requirements	227

8.14.4.2.LEBT-010:VAC-VGP-99999: Procedure of verification	228

8.15.	Test case LEBT-010:VAC-VGC-99999	230

8.15.1.	Gauge & Gauge Controller Verification: Support Environment.	230

8.15.2.	Gauge & Gauge Controller Verification: Configuration	230

8.15.3.	Gauge & Gauge Controller Verification: Setup	230

8.15.4.	Gauge & Gauge Controller Verification: Procedure	230

8.15.4.1.LEBT-010:VAC-VGC-99999: List of requirements	231

8.15.4.2.LEBT-010:VAC-VGC-99999: Procedure of verification	232

8.16.	Test case LEBT-010:VAC-VPG-20001	234

8.16.1.	Vacuum Pumping Group Verification: Support Environment.	234

8.16.2.	Vacuum Pumping Group Verification: Configuration	234

8.16.3.	Vacuum Pumping Group Verification: Setup	234

8.16.4.	Vacuum Pumping Group Verification: Procedure	234

8.16.4.1.LEBT-010:VAC-VPG-20001: List of requirements	235

8.16.4.2.LEBT-010:VAC-VPG-20001: Procedure of verification	236

8.17.	Test case LEBT-010:VAC-VVA-00041	252

8.17.1.	Angle Valves & Gates Valves Verification: Support Environment.	252

8.17.2.	Angle Valves & Gates Valves Verification: Configuration	252

8.17.3.	Angle Valves & Gates Valves Verification: Setup	252

8.17.4.	Angle Valves & Gates Valves Verification: Procedure	252

8.17.4.1.LEBT-010:VAC-VVA-00041: List of requirements	253

8.17.4.2.LEBT-010:VAC-VVA-00041: Procedure of verification	253

9.	Test Cases “:VAC-PLCIO-" (PLC tests)	262

9.1.	Test case LEBT-010:VAC-PLCIO-10001	262

9.1.1.	PLC Remote I/Os Verification: Support Environment.	262

9.1.2.	PLC Remote I/Os Verification: Configuration	262

9.1.3.	PLC Remote I/Os Verification: Setup	262

9.1.4.	PLC Remote I/Os Verification: Procedure	262

9.1.4.1.	LEBT-010:VAC-PLCIO-10001: List of requirements	263

9.1.4.2.	LEBT-010:VAC-PLCIO-10001: Procedure of verification	263

9.2.	Test case LEBT-010:VAC-PLCIO-01001	264

9.2.1.	PLC Remote I/Os Verification: Support Environment.	264

9.2.2.	PLC Remote I/Os Verification: Configuration	264

9.2.3.	PLC Remote I/Os Verification: Setup	264

9.2.4.	PLC Remote I/Os Verification: Procedure	264

9.2.4.1.	LEBT-010:VAC-PLCIO-01001: List of requirements	265

9.2.4.2.	LEBT-010:VAC-PLCIO-01001: Procedure of verification	265

10.	Glossary	266

11.	references	267

Document Revision history	268

list of tables

Table 1	 LEBT-010:VAC-VPSU-00000: Local Control (Part 1).	23

Table 2	ISRC-010:VAC-VPM-00011: Control & Monitoring.	26

Table 3	 ISRC-010:VAC-VVA-01100: Remote & Manual Control (Part 1).	29

Table 4	 ISRC-010:VAC-VVA-01100: Remote Control (Part 2).	30

Table 5	 ISRC-010:VAC-VVA-01100: First “Pressure” Interlock.	31

Table 6	 ISRC-010:VAC-VVA-01100: Second “Pressure” Interlock.	32

Table 7	 ISRC-010:VAC-VVA-01100: First “Hardware” Interlock.	33

Table 8	 ISRC-010:VAC-VVA-01100: Second “Hardware” Interlock.	34

Table 9	 ISRC-010:VAC-VVA-01100: Third “Hardware” Interlock.	35

Table 10	ISRC-010:VAC-VVA-01100: Pressure Interlock (Part 1).	36

Table 11	 ISRC-010:VAC-VVA-01100: Access Interlock (Part 1).	36

Table 12	ISRC-010:VAC-VVMC-01100: Control & Monitoring (Part 1).	40

Table 13	ISRC-010:VAC-VVMC-01100: Control & Monitoring (Part 2).	41

Table 14	 LEBT-010:VAC-VPDP-00031: Local Control (Part 1).	44

Table 15	 LEBT-010:VAC-VPDP-00031: Local Control (Part 2).	45

Table 16	 LEBT-010:VAC-VPDP-00031: Local Control (Part 3).	46

Table 17	 LEBT-010:VAC-VPDP-00031: Remote Control (Part 1).	46

Table 18	 LEBT-010:VAC-VPDP-00031: “Pressure” Interlock.	47

Table 19	 LEBT-010:VAC-VPDP-00031: “Hardware” Interlock.	48

Table 20	 LEBT-010:VAC-VVA-00031: Remote & Manual Control (Part 1).	51

Table 21	 LEBT-010:VAC-VVA-00031: Remote Control (Part 2).	52

Table 22	 LEBT-010:VAC-VVA-00031: First “Pressure” Interlock.	53

Table 23	 LEBT-010:VAC-VVA-00031: Second “Pressure” Interlock.	54

Table 24	LEBT-010:VAC-VVA-00031: First “Hardware” Interlock.	55

Table 25	LEBT-010:VAC-VVA-00031: Second “Hardware” Interlock.	56

Table 26	LEBT-010:VAC-VVA-00031: Third “Hardware” Interlock.	57

Table 27	LEBT-010:VAC-VGP-00021: Control & Monitoring (Part 1).	60

Table 28	LEBT-010:VAC-VGP-00021: Control & Monitoring (Part 2).	61

Table 29	LEBT-010:VAC-VPT-02100: Remote Control (Part 1).	64

Table 30	LEBT-010:VAC-VPT-02100: Remote Control (Part 2).	65

Table 31	 LEBT-010:VAC-VPT-02100: “Pressure” Interlock.	66

Table 32	 LEBT-010:VAC-VPT-02100: “Hardware” Interlock.	67

Table 33	LEBT-010:VAC-VVA-02100: Remote & Manual Control (Part 1).	69

Table 34	LEBT-010:VAC-VVA-02100: Remote Control (Part 2).	70

Table 35	LEBT-010:VAC-VVA-02100: First “Pressure” Interlock.	71

Table 36	LEBT-010:VAC-VVA-02100: Second “Pressure” Interlock.	72

Table 37	LEBT-010:VAC-VVA-02100: First “Hardware” Interlock.	73

Table 38	LEBT-010:VAC-VVA-02100: Second “Hardware” Interlock.	74

Table 39	LEBT-010:VAC-VVA-02100: Third “Hardware” Interlock.	75

Table 40	LEBT-010:VAC-VPT-03100: Remote Control (Part 1).	78

Table 41	LEBT-010:VAC-VPT-03100: Remote Control (Part 2).	79

Table 42	 LEBT-010:VAC-VPT-03100: “Pressure” Interlock.	80

Table 43	 LEBT-010:VAC-VPT-03100: “Hardware” Interlock.	81

Table 44	LEBT-010:VAC-VVA-03100: Remote & Manual Control (Part 1).	83

Table 45	LEBT-010:VAC-VVA-03100: Remote Control (Part 2).	84

Table 46	LEBT-010:VAC-VVA-03100: First “Pressure” Interlock.	85

Table 47	LEBT-010:VAC-VVA-03100: Second “Pressure” Interlock.	86

Table 48	LEBT-010:VAC-VVA-03100: First “Hardware” Interlock.	87

Table 49	LEBT-010:VAC-VVA-03100: Second “Hardware” Interlock.	88

Table 50	LEBT-010:VAC-VVA-03100: Third “Hardware” Interlock.	89

Table 51	LEBT-010:VAC-VGP-10000: Control & Monitoring (Part 1).	92

Table 52	LEBT-010:VAC-VGP-10000: Control & Monitoring (Part 2).	93

Table 53	LEBT-010:VAC-VGC-10000: Control & Monitoring (Part 1).	96

Table 54	LEBT-010:VAC-VGC-10000: Control & Monitoring (Part 2).	97

Table 55	LEBT-010:VAC-VGD-10000: Control & Monitoring (Part 1).	100

Table 56	LEBT-010:VAC-VGD-10000: Control & Monitoring (Part 2).	101

Table 57	LEBT-010:VAC-VPG-10001: Pump-Down Atmospheric Pressure (Part 1).	104

Table 58	LEBT-010:VAC-VPG-10001: Pump-Down Atmospheric Pressure (Part 2).	105

Table 59	LEBT-010:VAC-VPG-10001: Normal Starting Sequence [sector under vacuum] (Part 1)	106

Table 60	LEBT-010:VAC-VPG-10001: Normal Starting Sequence  [sector under vacuum] (Part 2)	107

Table 61	LEBT-010:VAC-VPG-10001: Normal Stopping Sequence [sector under vacuum] (Part 1)	108

Table 62	LEBT-010:VAC-VPG-10001: Normal Stopping Sequence [sector under vacuum] (Part 2)	109

Table 63	LEBT-010:VAC-VPG-10001: Normal Stopping Sequence [sector under vacuum] (Part 3)	110

Table 64	LEBT-010:VAC-VPG-10001: Maintenance (Leak Detection) Sequence.	111

Table 65	LEBT-010:VAC-VPG-10001: Local Protections (Part 1).	112

Table 66	LEBT-010:VAC-VPG-10001: Local Protections (Part 2).	113

Table 67	LEBT-010:VAC-VPG-10001: Local Protections (Part 3).	114

Table 68	LEBT-010:VAC-VPG-10001: Local Protections (Part 4 - Pressure Interlock).	115

Table 69	LEBT-010:VAC-VPG-10001: Local Protections (Part 5 - Pressure Interlock).	116

Table 70	LEBT-010:VAC-VPG-10001: Local Protections (Part 6).	117

Table 71	LEBT-010:VAC-VPG-10001: Local Protections (Part 7).	118

Table 72	LEBT-010:VAC-VPM-00011: Control & Monitoring.	122

Table 73	 LEBT-010:VAC-VVA-01100: Remote & Manual Control (Part 1).	125

Table 74	 LEBT-010:VAC-VVA-01100: Remote Control (Part 2).	126

Table 75	 LEBT-010:VAC-VVA-01100: First “Pressure” Interlock.	127

Table 76	 LEBT-010:VAC-VVA-01100: Second “Pressure” Interlock.	128

Table 77	LEBT-010:VAC-VVA-01100: First “Hardware” Interlock.	129

Table 78	LEBT-010:VAC-VVA-01100: Second “Hardware” Interlock.	130

Table 79	LEBT-010:VAC-VVA-01100: Third “Hardware” Interlock.	131

Table 80	LEBT-010:VAC-VVA-01100: Access Interlock (Part 1).	132

Table 81	LEBT-010:VAC-VVMC-01100: Control & Monitoring (Part 1).	136

Table 82	LEBT-010:VAC-VVMC-01100: Control & Monitoring (Part 2).	137

Table 83	LEBT-010:VAC-VGR-10000: Control & Monitoring.	140

Table 84	 LEBT-010:VAC-VPDP-00071: Local Control (Part 1).	144

Table 85	 LEBT-010:VAC-VPDP-00071: Local Control (Part 2).	145

Table 86	 LEBT-010:VAC-VPDP-00071: Local Control (Part 3).	146

Table 87	 LEBT-010:VAC-VPDP-00071: Remote Control (Part 1).	146

Table 88	 LEBT-010:VAC-VPDP-00071: “Pressure” Interlock.	147

Table 89	 LEBT-010:VAC-VPDP-00071: “Hardware” Interlock.	148

Table 90	 LEBT-010:VAC-VVA-00071: Remote & Manual Control (Part 1).	151

Table 91	 LEBT-010:VAC-VVA-00071: Remote Control (Part 2).	152

Table 92	 LEBT-010:VAC-VVA-00071: First “Pressure” Interlock.	153

Table 93	 LEBT-010:VAC-VVA-00071: Second “Pressure” Interlock.	154

Table 94	LEBT-010:VAC-VVA-00071: First “Hardware” Interlock.	155

Table 95	LEBT-010:VAC-VVA-00071: Second “Hardware” Interlock.	156

Table 96	LEBT-010:VAC-VVA-00071: Third “Hardware” Interlock.	157

Table 97	LEBT-010:VAC-VGP-00081: Control & Monitoring (Part 1).	160

Table 98	LEBT-010:VAC-VGP-00081: Control & Monitoring (Part 2).	161

Table 99	LEBT-010:VAC-VPT-06100: Remote Control (Part 1).	164

Table 100	LEBT-010:VAC-VPT-06100: Remote Control (Part 2).	165

Table 101	 LEBT-010:VAC-VPT-06100: “Pressure” Interlock.	166

Table 102	 LEBT-010:VAC-VPT-06100: “Hardware” Interlock.	167

Table 103	LEBT-010:VAC-VVA-06100: Remote & Manual Control (Part 1).	169

Table 104	LEBT-010:VAC-VVA-06100: Remote Control (Part 2).	170

Table 105	LEBT-010:VAC-VVA-06100: First “Pressure” Interlock.	171

Table 106	LEBT-010:VAC-VVA-06100: Second “Pressure” Interlock.	172

Table 107	LEBT-010:VAC-VVA-06100: First “Hardware” Interlock.	173

Table 108	LEBT-010:VAC-VVA-06100: Second “Hardware” Interlock.	174

Table 109	LEBT-010:VAC-VVA-06100: Third “Hardware” Interlock.	175

Table 110	LEBT-010:VAC-VPT-07100: Remote Control (Part 1).	178

Table 111	LEBT-010:VAC-VPT-07100: Remote Control (Part 2).	179

Table 112	 LEBT-010:VAC-VPT-07100: “Pressure” Interlock.	180

Table 113	 LEBT-010:VAC-VPT-07100: “Hardware” Interlock.	181

Table 114	LEBT-010:VAC-VVA-07100: Remote & Manual Control (Part 1).	183

Table 115	LEBT-010:VAC-VVA-07100: Remote Control (Part 2).	184

Table 116	LEBT-010:VAC-VVA-07100: First “Pressure” Interlock.	185

Table 117	LEBT-010:VAC-VVA-07100: Second “Pressure” Interlock.	186

Table 118	LEBT-010:VAC-VVA-07100: First “Hardware” Interlock.	187

Table 119	LEBT-010:VAC-VVA-07100: Second “Hardware” Interlock.	188

Table 120	LEBT-010:VAC-VVA-07100: Third “Hardware” Interlock.	189

Table 121	LEBT-010:VAC-VGP-30000: Control & Monitoring (Part 1).	192

Table 122	LEBT-010:VAC-VGP-30000: Control & Monitoring (Part 2).	193

Table 123	LEBT-010:VAC-VGC-30000: Control & Monitoring (Part 1).	196

Table 124	LEBT-010:VAC-VGC-30000: Control & Monitoring (Part 2).	197

Table 125	LEBT-010:VAC-VPT-99998: Remote Control (Part 1).	200

Table 126	LEBT-010:VAC-VPT-99998: Remote Control (Part 2).	201

Table 127	 LEBT-010:VAC-VPT-99998: “Pressure” Interlock.	202

Table 128	 LEBT-010:VAC-VPT-99998: “Hardware” Interlock.	203

Table 129	LEBT-010:VAC-VVA-99998: Remote & Manual Control (Part 1).	205

Table 130	LEBT-010:VAC-VVA-99998: Remote Control (Part 2).	206

Table 131	LEBT-010:VAC-VVA-99998: First “Pressure” Interlock.	207

Table 132	LEBT-010:VAC-VVA-99998: Second “Pressure” Interlock.	208

Table 133	LEBT-010:VAC-VVA-99998: First “Hardware” Interlock.	209

Table 134	LEBT-010:VAC-VVA-99998: Second “Hardware” Interlock.	210

Table 135	LEBT-010:VAC-VVA-99998: Third “Hardware” Interlock.	211

Table 136	LEBT-010:VAC-VPT-99999: Remote Control (Part 1).	214

Table 137	LEBT-010:VAC-VPT-99999: Remote Control (Part 2).	215

Table 138	 LEBT-010:VAC-VPT-99999: “Pressure” Interlock.	216

Table 139	 LEBT-010:VAC-VPT-99999: “Hardware” Interlock.	217

Table 140	LEBT-010:VAC-VVA-99999: Remote & Manual Control (Part 1).	219

Table 141	LEBT-010:VAC-VVA-99999: Remote Control (Part 2).	220

Table 142	LEBT-010:VAC-VVA-99999: First “Pressure” Interlock.	221

Table 143	LEBT-010:VAC-VVA-99999: Second “Pressure” Interlock.	222

Table 144	LEBT-010:VAC-VVA-99999: First “Hardware” Interlock.	223

Table 145	LEBT-010:VAC-VVA-99999: Second “Hardware” Interlock.	224

Table 146	LEBT-010:VAC-VVA-99999: Third “Hardware” Interlock.	225

Table 147	LEBT-010:VAC-VGP-99999: Control & Monitoring (Part 1).	228

Table 148	LEBT-010:VAC-VGP-99999: Control & Monitoring (Part 2).	229

Table 149	LEBT-010:VAC-VGC-99999: Control & Monitoring (Part 1).	232

Table 150	LEBT-010:VAC-VGC-99999: Control & Monitoring (Part 2).	233

Table 151	LEBT-010:VAC-VPG-20001: Pump-Down Atmospheric Pressure (Part 1).	236

Table 152	LEBT-010:VAC-VPG-20001: Pump-Down Atmospheric Pressure (Part 2).	237

Table 153	LEBT-010:VAC-VPG-20001: Normal Starting Sequence [sector under vacuum] (Part 1)	238

Table 154	LEBT-010:VAC-VPG-20001: Normal Starting Sequence  [sector under vacuum] (Part 2)	239

Table 155	LEBT-010:VAC-VPG-20001: Normal Stopping Sequence [sector under vacuum] (Part 1)	240

Table 156	LEBT-010:VAC-VPG-20001: Normal Stopping Sequence [sector under vacuum] (Part 2)	241

Table 157	LEBT-010:VAC-VPG-20001: Normal Stopping Sequence [sector under vacuum] (Part 3)	242

Table 158	LEBT-010:VAC-VPG-20001: Maintenance (Leak Detection) Sequence.	243

Table 159	LEBT-010:VAC-VPG-20001: Local Protections (Part 1).	244

Table 160	LEBT-010:VAC-VPG-20001: Local Protections (Part 2).	245

Table 161	LEBT-010:VAC-VPG-20001: Local Protections (Part 3).	246

Table 162	LEBT-010:VAC-VPG-20001: Local Protections (Part 4 - Pressure Interlock).	247

Table 163	LEBT-010:VAC-VPG-20001: Local Protections (Part 5 - Pressure Interlock).	248

Table 164	LEBT-010:VAC-VPG-20001: Local Protections (Part 6).	249

Table 165	LEBT-010:VAC-VPG-20001: Local Protections (Part 7).	250

Table 166	LEBT-010:VAC-VVA-00041: Remote & Manual Control (Part 1).	253

Table 167	LEBT-010:VAC-VVA-00041: Remote Control (Part 2).	254

Table 168	LEBT-010:VAC-VVA-00041: Automatic Control (Part 1).	255

Table 169	 LEBT-010:VAC-VVA-00041: First “Pressure” Interlock.	256

Table 170	 LEBT-010:VAC-VVA-00041: Second “Pressure” Interlock.	257

Table 171	LEBT-010:VAC-VVA-00041: First “Hardware” Interlock.	258

Table 172	LEBT-010:VAC-VVA-00041: Second “Hardware” Interlock.	259

Table 173	LEBT-010:VAC-VVA-00041: Third “Hardware” Interlock.	260

Table 174	 LEBT-010:VAC-PLCIO-10001: Hardware Fault Detection (Part 1).	263

Table 175	 LEBT-010:VAC-PLCIO-01001: Hardware Fault Detection (Part 1).	265

list of Figures

No table of figures entries found.

# Introduction

This document lists and describes verification tests that have to be achieved during the commissioning of the LEBT Vacuum Control Systems [3].

# Issuing organisation

This document is written by Integrated Control Division from the Machine Directorate of ESS.

# System characteristics

## System purpose

The Proton Beam Vacuum Control System [1] is the system that controls vacuum equipment’s installed on the LINAC at ESS.

## System overview

The Proton Beam Vacuum System [1] is split into several subsystems. Each of these subsystems has its own control sub-system.

This document is dedicated to the LEBT Vacuum Control subsystem [3].

Vacuum devices that this document refers to are represented on vacuum layout [8] of the LEBT Vacuum System.

LEBT Vacuum Control System is listed into the ESS Functional Breakdown Structure [10]: =ESS.ACC.G01.G01.

## Notation for description

Devices that this document refers to are identified with their device mnemonic defined by the “Vacuum Symbols and ICS naming” [5] document and by their names issued from the ESS Naming Service [11].

Hardware electrical interfaces that this document refers to are defined by the electrical diagram designed [6] by Vacuum Group, part of the Specialized Technical Services Group of the Accelerator Division of the Machine Directorate

# Verification identification

Any anomalies founds during the verification tests shall be identified and solved. The following test won’t be fulfilled until the entire test is compliant with the expected result.

## Support Environment

All the vacuum components that this document refers to are located in the accelerator tunnel [10]: +ESS.G01.090.1001.100.

All vacuum control equipment and control equipment that this document refers to are located in a rack in the Front End building [10]: +ESS.G01.090.5005.102.001.

Involved personnel to perform these tests are both ICS division and vacuum group.

The verification shall involve at least one person on site to validate that the remotely controlled hardware device targeted by the test is the desired one to be actuated. This person is preferably the representative of the Vacuum Group.

The verification test shall involve at least one person on the control room or using control room operation screen to assess status feedback on the GUI screen. This person is preferably the representative of the ICS Division.

- Responsible officer for this test is the Vacuum Group or its representative.

## Configuration

Configuration to be checked during the validation test:

- Vacuum System: Proton Beam Vacuum System (=ESS.ACC.G01.K01).

- Vacuum Sub-system: LEBT Vacuum System (=ESS.ACC.G01.G01.K01).

- Vacuum Layout: ISRC + LEBT Vacuum Diagram [8].

- Electrical Diagram: Accelerator Vacuum Controls - Wiring diagrams vacuum control racks [6].

Control configuration:

- Graphical Interface: Proton-Beam-Vacuum.bob

- EPICS IOC:

  - VacS-ACCV:VAC-IOC-11010.

  - VacS-ACCV:VAC-IOC-DAQ001

- PLC Project: =ESS.ACC.G01.K01.ap14.

## Setup

Vacuum system shall be leak tight and ready to be pumped to perform the following tests.

# Test Cases “LEBT-010:VAC-VPSU" (Rack Power Supply)

## Test case LEBT-010:VAC-VPSU-00000

### Support Environment.

See 4.1 for generic support environment.

### Configuration

See 4.2 for generic configuration.

### Setup

See 4.3 for generic setup.

All the vacuum control equipment shall be disconnected from the power strip and any device should be energized before starting tests describe by Table 1.

### Primary pump & Primary Pump Controller Verification: Procedure

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VPSU-00010: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| No requirements | No requirements | No requirements | No requirements | No requirements | No requirements |

#### LEBT-010:VAC-VPSU-00000: Procedure of verification

Table 1		LEBT-010:VAC-VPSU-00000: Local Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPSU-00010_VT-00001 | Verification of the 3-phases power supply. | Tripp -FC41 in ESS.G01.90.5005.102.001.U10. | Assess the “400VAC Error”. | □ |
| LEBT-010:VAC-VPSU-00010_VT-00002 | Verification of the DC power supply - Warning Limit. | Connect a calibrated load on the 24VDC power supply. | Assess the “24VDC Warning. | □ |
| LEBT-010:VAC-VPSU-00010_VT-00003 | Verification of the DC power supply - Error. | Connect a calibrated load on the 24VDC power distribution module: -QB10 in ESS.G01.90.5005.102.001.U10. | Assess the “24VDC Error”. |  |
|  |  | Wait the automatic reset of the error. | Assess the “Auto-Reset” status. | □ |
|  |  | Disconnect the calibrated load. | Assess that the error disappear. | □ |
|  |  | Re-connect the calibrated load to trip the power supply and wait the Auto-Reset time-out. | Assess the “24VDC Error”. Assess the “Auto-Reset ” failure status on the GUI panel. | □ |
| LEBT-010:VAC-VPSU-00010_VT-00004 |  | Reset the error from the GUI. | Assess that the “Error” and “CB Fail” status has disappeared on the GUI panel. | □ |

# Test Cases “ISRC-010:VAC" (Ion Source)

## Test case ISRC-010:VAC-VPM-00011

### Pressure Manometer Verification: Support Environment.

See 4.1 for generic support environment.

### Pressure Manometer Verification: Configuration

See 4.2 for generic configuration.

### Pressure Manometer Verification: Setup

See 4.3 for generic setup.

### Pressure Manometer Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the device.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### ISRC-010:VAC-VPM-00011: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| ISRC-010:VAC-VPM-00011_CR.01 | ISRC-010:VAC-VPM-00011_MR.01 | ISRC-010:VAC-VPM-00011_DAR.01 | ISRC-010:VAC-VPM-00011_CsR.01 | ISRC-010:VAC-VPM-00011_SR.01 | ISRC-010:VAC-VPM-00011_IR.01 |
|  | ISRC-010:VAC-VPM-00011_MR.02 |  |  |  |  |

#### ISRC-010:VAC-VPM-00011: Procedure of verification

ISRC-010:VAC-VPM-00011_VT-00001: Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 2	ISRC-010:VAC-VPM-00011: Control & Monitoring.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| ISRC-010:VAC-VPM-00011_VT-00002 | Assess the pressure value. | Read pressure on the GUI panel. | Assess the pressure on the GUI panel. | □ |
|  |  |  | Corroborate the pressure on the GUI panel with the pressure display on the monometer. | □ |
| ISRC-010:VAC-VPM-00011_VT-00003 | Verify the pressure archiving. | Open archiving appliance. | Assess the value of the archived pressure. | □ |
| ISRC-010:VAC-VPM-00011_VT-00004 | Test the low pressure alarm. | Create or simulate a drop-down of the pressure read by the pressure manometer. | Assess that the alarm is active on the control room. | □ |
|  |  | It is also possible to modify the alarm threshold. | Write down the initial threshold before modification: _______________________________________ | □ |
|  |  |  | Write down the threshold set for the test: _______________________________________ | □ |
|  |  |  | Assess that the alarm is active on the control room. | □ |
|  |  |  | Write down value set after the test: ______________________________________ | □ |

## Test case ISRC-010:VAC-VVA-01100

### Angle Valves & Gates Valves Verification: Support Environment.

See 4.1 for generic support environment.

### Angle Valves & Gates Valves Verification: Configuration

See 4.2 for generic configuration.

### Angle Valves & Gates Valves Verification: Setup

See 4.3 for generic setup.

Angle valve or gate valve shall be connected and shall not be open before starting the test.

A simulator can be used instead of the valve to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the valve.

The GUI panel shall show that the valve to be check is free of errors before starting the verification procedure.

### Angle Valves & Gates Valves Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the valve.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### ISRC-010:VAC-VVA-01100: List of requirements

| Reference to the requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| ISRC-010:VAC-VVA-01100_CR.01 | ISRC-010:VAC-VVA-01100_MR.01 | ISRC-010:VAC-VVA-01100_DAR.01 | ISRC-010:VAC-VVA-01100_CsR.01 | ISRC-010:VAC-VVA-01100_SR.01 | ISRC-010:VAC-VVA-01100_IR.01 |
| ISRC-010:VAC-VVA-01100_CR.02 | ISRC-010:VAC-VVA-01100_MR.02 | ISRC-010:VAC-VVA-01100_DAR.02 |  | LEBT-010:VAC-VEG-1001_SR.01 |  |
| ISRC-010:VAC-VVA-01100_CR.03 | ISRC-010:VAC-VVA-01100_MR.03 | ISRC-010:VAC-VVA-01100_DAR.03 |  |  |  |
|  | ISRC-010:VAC-VVA-01100_MR.04 |  |  |  |  |
|  | ISRC-010:VAC-VVA-01100_MR.05 |  |  |  |  |

#### ISRC-010:VAC-VVA-01100: Procedure of verification

ISRC-010:VAC-VVA-01100_VT-00001: Pump Cable Number __________________________________________(Check cable labelling on both side of the cable).

Table 3		ISRC-010:VAC-VVA-01100: Remote & Manual Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| ISRC-010:VAC-VVA-01100_VT-00002 | Assess the closed status of the valve. | No action required because the valve shall already be closed. | Assess the “Close” status on the GUI panel. | □ |
| ISRC-010:VAC-VVA-01100_VT-00003 | Assess the “Undefined” status of the valve. | Disconnect the control cable from the connector on the valve. Wait that “Undefined” time-out elapsed. | Assess the “Undefined” status on the GUI panel. | □ |

Table 4		ISRC-010:VAC-VVA-01100: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| ISRC-010:VAC-VVA-01100_VT-00004 | Verify the manual remote control of the valve. | Set “Manual” mode using the detailed GUI panel of the valve. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before opening the valve. | □ |
| ISRC-010:VAC-VVA-01100_VT-00005 | Verify the opening function. | Verify that there are no active interlocks applied to the valve. Open the valve through the GUI panel. | Assess the “Open” status on the GUI panel. | □ |
| ISRC-010:VAC-VVA-01100_VT-00006 | Verify the closing function. | Close the valve through the GUI panel. | Assess the “Close” status on the GUI panel. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 5		ISRC-010:VAC-VVA-01100: First “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| ISRC-010:VAC-VVA-01100_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| ISRC-010:VAC-VVA-01100_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| ISRC-010:VAC-VVA-01100_VT-00009 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| ISRC-010:VAC-VVA-01100_VT-00010 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| ISRC-010:VAC-VVA-01100_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| ISRC-010:VAC-VVA-01100_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| ISRC-010:VAC-VVA-01100_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 6		ISRC-010:VAC-VVA-01100: Second “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| ISRC-010:VAC-VVA-01100_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| ISRC-010:VAC-VVA-01100_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| ISRC-010:VAC-VVA-01100_VT-00016 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| ISRC-010:VAC-VVA-01100_VT-00017 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| ISRC-010:VAC-VVA-01100_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| ISRC-010:VAC-VVA-01100_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| ISRC-010:VAC-VVA-01100_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 7		ISRC-010:VAC-VVA-01100: First “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| ISRC-010:VAC-VVA-01100_VT-00021 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| ISRC-010:VAC-VVA-01100_VT-00022 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| ISRC-010:VAC-VVA-01100_VT-00023 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| ISRC-010:VAC-VVA-01100_VT-00024 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| ISRC-010:VAC-VVA-01100_VT-00025 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| ISRC-010:VAC-VVA-01100_VT-00026 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| ISRC-010:VAC-VVA-01100_VT-00027 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 8		ISRC-010:VAC-VVA-01100: Second “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| ISRC-010:VAC-VVA-01100_VT-00028 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| ISRC-010:VAC-VVA-01100_VT-00029 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| ISRC-010:VAC-VVA-01100_VT-00030 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| ISRC-010:VAC-VVA-01100_VT-00031 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| ISRC-010:VAC-VVA-01100_VT-00032 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| ISRC-010:VAC-VVA-01100_VT-00033 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| ISRC-010:VAC-VVA-01100_VT-00034 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 9		ISRC-010:VAC-VVA-01100: Third “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| ISRC-010:VAC-VVA-01100_VT-00035 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| ISRC-010:VAC-VVA-01100_VT-00036 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| ISRC-010:VAC-VVA-01100_VT-00037 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| ISRC-010:VAC-VVA-01100_VT-00038 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| ISRC-010:VAC-VVA-01100_VT-00039 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| ISRC-010:VAC-VVA-01100_VT-00040 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| ISRC-010:VAC-VVA-01100_VT-00041 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

Table 10	ISRC-010:VAC-VVA-01100: Pressure Interlock (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| ISRC-010:VAC-VVA-01100_VT-00042 | Verify the closure of the valve in case of raise of the pressure into the first vacuum sector. | Start the vacuum system and set the nominal conditions to produce beam. Open the valve. | Assess that the valve is open. | □ |
|  |  | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VGC-10000 (Relay 8) Write down the actual setting of the relay:___________________________________________________________ |  | □ |
|  |  | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the closure of the valve. | □ |
|  |  | Re-establish the interlock. | Interlock is healthy. | □ |
|  |  |  | Write down the threshold set after the test: _______________________________________ | □ |

Table 11		ISRC-010:VAC-VVA-01100: Access Interlock (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| ISRC-010:VAC-VVA-01100_VT-00043 | Verify the closure of the valve in case of access of person in the tunnel. | Start the vacuum system and set the nominal conditions to produce beam. Open the valve. | Assess that the valve is open. | □ |
|  |  | Request an access to the MCR or simulate it according to the electrical diagram [6]. | Assess that the valve closes. | □ |

## Test case ISRC-010:VAC-VVMC-01100

### Mass Flow Meter & Mass Flow Meter Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Mass Flow Meter & Mass Flow Meter Controller Verification: Configuration

See 4.2 for generic configuration.

### Mass Flow Meter & Mass Flow Meter Controller Verification: Setup

See 4.3 for generic setup.

Mass flow meter shall be under the nominal vacuum range before proceeding to the test.

Mass flow meter shall be connected and shall be close before starting the test.

Mass flow meter controller shall be energized and shall not display any error to start the verification procedure.

### Mass Flow Meter & Mass Flow Meter Controller Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the mass flow meter.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### ISRC-010:VAC-VVMC-01100: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| ISRC-010:VAC-VVMC-01100_CR.01 | ISRC-010:VAC-VVMC-01100_MR.01 | ISRC-010:VAC-VVMC-01100_DAR.01 | ISRC-010:VAC-VEVMC-01100_CsR.01 | ISRC-010:VAC-VEVMC-01100_SR.01 | ISRC-010:VAC-VEVMC-01100_IR.01 |
|  | ISRC-010:VAC-VVMC-01100_MR.02 |  | ISRC-010:VAC-VEVMC-02200_CsR.01 | ISRC-010:VAC-VEVMC-02200_SR.01 | ISRC-010:VAC-VEVMC-02200_IR.01 |
|  | ISRC-010:VAC-VVMC-01100_MR.03 |  | ISRC-010:VAC-VEVMC-10001_CsR.01 | ISRC-010:VAC-VEVMC-10001_SR.01 | ISRC-010:VAC-VEVMC-10001_IR.01 |
|  | ISRC-010:VAC-VVMC-01100_MR.04 |  |  |  |  |
|  | ISRC-010:VAC-VVMC-01100_MR.05 |  |  |  |  |
|  | ISRC-010:VAC-VVMC-01100_MR.06 |  |  |  |  |
|  | ISRC-010:VAC-VVMC-01100_MR.07 |  |  |  |  |
|  | ISRC-010:VAC-VVMC-01100_MR.08 |  |  |  |  |
|  | ISRC-010:VAC-VVMC-01100_MR.09 |  |  |  |  |
|  | ISRC-010:VAC-VVMC-01100_MR.10 |  |  |  |  |
|  | ISRC-010:VAC-VVMC-01100_MR.11 |  |  |  |  |

#### ISRC-010:VAC-VVMC-01100: Procedure of verification

ISRC-010:VAC-VVMC-01100_VT-00001: Pump Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 12	ISRC-010:VAC-VVMC-01100: Control & Monitoring (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| ISRC-010:VAC-VVMC-01100_VT-00002 | Assess the partial opening. | Partially open the mass flow meter through the GUI panel. | Assess the partial opening on the GUI panel. | □ |
|  |  |  | Assess the partial opening on the mass flow meter controller | □ |
| ISRC-010:VAC-VVMC-01100_VT-00003 | Assess the partial closing. | Partially close the mass flow meter through the GUI panel. | Assess the partial closing on the GUI panel. | □ |
|  |  |  | Assess the partial closing on the mass flow meter controller | □ |

Table 13	ISRC-010:VAC-VVMC-01100: Control & Monitoring (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| ISRC-010:VAC-VVMC-01100_VT-00004 | Verify that the parameters of the mass flow meter can be remotely modified. | Choose a parameter relative to the gauge. | Write down the value of the parameter before the modification: ________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : ________________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: ________________________________________ | □ |
| ISRC-010:VAC-VVMC-01100_VT-00005 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. | Write down the value of the parameter before the modification: ________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : ________________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: ________________________________________ | □ |

# Test Cases “LEBT-010:VAC" (First Vacuum Sector)

## Test case LEBT-010:VAC-VPDP-00031

### Primary Pump & Primary Pump Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Primary Pump & Primary Pump Controller Verification: Configuration

See 4.2 for generic configuration.

### Primary Pump & Primary Pump Controller Verification: Setup

See 4.3 for generic setup.

Primary pump shall be connected and shall not be running before starting the test.

Primary pump controller shall be energized, shall not display any error and control switch shall be on “PLC” position to start the verification procedure.

The GUI panel shall show that the controller to be check is free of errors before starting the verification procedure.

### Primary Pump & Primary Pump Controller Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the pump.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VPDP-00031: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VPDP-00031_CR.01 | LEBT-010:VAC-VPDP-00031_MR.01 | LEBT-010:VAC-VPDP-00031_DAR.01 | LEBT-010:VAC-VPDP-00031_CsR.01 | LEBT-010:VAC-VPDP-00031_SR.01 | LEBT-010:VAC-VPDP-00031_IR.01 |
| LEBT-010:VAC-VPDP-00031_CR.02 | LEBT-010:VAC-VPDP-00031_MR.02 |  |  |  |  |
| LEBT-010:VAC-VPDP-00031_CR.03 | LEBT-010:VAC-VPDP-00031_MR.03 |  |  |  |  |
| LEBT-010:VAC-VPDP-00031_CR.04 | LEBT-010:VAC-VPDP-00031_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VPDP-00031_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VPDP-00031_MR.06 |  |  |  |  |

#### LEBT-010:VAC-VPDP-00031: Procedure of verification

LEBT-010:VAC-VPDP-00031_VT-00001: Pump Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 14		LEBT-010:VAC-VPDP-00031: Local Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPDP-00031_VT-00002 | Control the pump disconnection protection. | On the tunnel, after having verified that the pump is not running, disconnect the power supply connector. | Assess the corresponding error on the GUI panel: “Pump Not Connected”. | □ |
|  |  |  | Assess the corresponding error on the primary pump controller: the LED “Cable Connected” is off. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00003 | Reset the pump disconnected error. | After having assessed the disconnected error, reconnect the power supply connector. Reset the error from the GUI. | Assess that the “Pump Not Connected” error has disappeared on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Cable Connected” is on. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00004 | Assess the “Local Control” status. | Actuate the “Control” switch to the “Local” position on the primary pump controller. | Assess the “Local” Status on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Local Control” is on. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00005 | Start the pump by the primary pump controller. | Make sure that the system is in a safe condition before starting the pump. | Assess that the system is in a safe condition to start the pump. | □ |
|  |  | Actuate the “Control” switch to the “ON” position on the primary pump controller. | Verify that the pump in running on the tunnel. | □ |
|  |  |  | Assess the “On” status on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Pump ON” is on. | □ |

Table 15		LEBT-010:VAC-VPDP-00031: Local Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPDP-00031_VT-00006 | Stop the pump by the primary pump controller. | Actuate the “Control” switch to the “OFF” position on the primary pump controller. | Assess the “Off” status on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Pump ON” is off. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00007 | Verify the error status. | Open primary pump controller crate and trip the circuit breaker. Close primary pump controller crate. Actuate “Control” switch to the “ON” position on the primary pump controller. Wait error timeout. | Assess the “CB Fail” status on the GUI panel. | □ |
|  |  |  | Assess the “Error” status on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Error” is on. | □ |
|  |  |  | Actuate the “Control” switch to the “OFF” position on the primary pump controller. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00008 | Eliminate the previous error. | Actuate “Control” switch to the “OFF” position on the primary pump controller. Open primary pump controller crate, close the circuit breaker and close primary pump controller crate. | Circuit breaker is healthy and the “Error” LED is on. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00009 | Reset the pump error (remotely). | Reset the error from the GUI. | Assess that the “Error” and “CB Fail” status has disappeared on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Error” is off. | □ |

Table 16		LEBT-010:VAC-VPDP-00031: Local Control (Part 3).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPDP-00031_VT-00010 | Verify the “Remote” status. | Actuate the “Control” switch to the “PLC” position on the primary pump controller. | Assess the “Remote” status on the GUI panel: “Local” status shall have disappeared. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “PLC Control” is on and the LED “Local Control” is off. | □ |

Table 17		LEBT-010:VAC-VPDP-00031: Remote Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPDP-00031_VT-00011 | Verify the manual remote control of the pump. | Set “Manual” mode using the detailed GUI panel of the pump. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before starting the pump. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00012 | Start the primary pump remotely. | Start the primary pump through the GUI command | Assess the “On” status on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Pump ON” is on. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00013 | Stop the primary pump remotely. | Stop the primary pump through the GUI command | Assess the “Off” status on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Pump ON” is off. | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 18		LEBT-010:VAC-VPDP-00031: “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPDP-00031_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VPDP-00031_VT-00009 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00010 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 19		LEBT-010:VAC-VPDP-00031: “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPDP-00031_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  |  |
| LEBT-010:VAC-VPDP-00031_VT-00016 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00017 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPDP-00031_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VVA-00031

### Angle Valves & Gates Valves Verification: Support Environment.

See 4.1 for generic support environment.

### Angle Valves & Gates Valves Verification: Configuration

See 4.2 for generic configuration.

### Angle Valves & Gates Valves Verification: Setup

See 4.3 for generic setup.

Angle valve or gate valve shall be connected and shall not be open before starting the test.

A simulator can be used instead of the valve to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the valve.

The GUI panel shall show that the valve to be check is free of errors before starting the verification procedure.

### Angle Valves & Gates Valves Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the valve.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VVA-00031: List of requirements

| Reference to the requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VVA-00031_CR.01 | LEBT-010:VAC-VVA-00031_MR.01 | LEBT-010:VAC-VVA-00031_DAR.01 | LEBT-010:VAC-VVA-00031_CsR.01 | LEBT-010:VAC-VVA-00031_SR.01 | LEBT-010:VAC-VVA-00031_IR.01 |
| LEBT-010:VAC-VVA-00031_CR.02 | LEBT-010:VAC-VVA-00031_MR.02 | LEBT-010:VAC-VVA-00031_DAR.02 |  |  |  |
|  | LEBT-010:VAC-VVA-00031_MR.03 | LEBT-010:VAC-VVA-00031_DAR.03 |  |  |  |
|  | LEBT-010:VAC-VVA-00031_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VVA-00031_MR.05 |  |  |  |  |

#### LEBT-010:VAC-VVA-00031: Procedure of verification

LEBT-010:VAC-VVA-00031_VT-00001: Valve Cable Number __________________________________________(Check cable labelling on both side of the cable).

Table 20		LEBT-010:VAC-VVA-00031: Remote & Manual Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00031_VT-00002 | Assess the closed status of the valve. | No action required because the valve shall already be closed. | Assess the “Close” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-00031_VT-00003 | Assess the “Undefined” status of the valve. | Disconnect the control cable from the connector on the valve. Wait that “Undefined” time-out elapsed. | Assess the “Undefined” status on the GUI panel. | □ |

Table 21		LEBT-010:VAC-VVA-00031: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00031_VT-00004 | Verify the manual remote control of the valve. | Set “Manual” mode using the detailed GUI panel of the valve. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before opening the valve. | □ |
| LEBT-010:VAC-VVA-00031_VT-00005 | Verify the opening function. | Verify that there are no active interlocks applied to the valve. Open the valve through the GUI panel. | Assess the “Open” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-00031_VT-00006 | Verify the closing function. | Close the valve through the GUI panel. | Assess the “Close” status on the GUI panel. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 22		LEBT-010:VAC-VVA-00031: First “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00031_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-00031_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-00031_VT-00009 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00031_VT-00010 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00031_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00031_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00031_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 23		LEBT-010:VAC-VVA-00031: Second “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00031_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-00031_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VGP-00021 (Relay 1) _____________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-00031_VT-00016 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00031_VT-00017 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00031_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00031_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00031_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 24	LEBT-010:VAC-VVA-00031: First “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00031_VT-00021 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-00031_VT-00022 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-VAC:VPDP-00031 (Nominal Speed) _____________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-00031_VT-00023 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00031_VT-00024 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00031_VT-00025 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00031_VT-00026 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00031_VT-00027 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 25	LEBT-010:VAC-VVA-00031: Second “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00031_VT-00028 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-00031_VT-00029 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-00031_VT-00030 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00031_VT-00031 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00031_VT-00032 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00031_VT-00033 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00031_VT-00034 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 26	LEBT-010:VAC-VVA-00031: Third “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00031_VT-00035 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-00031_VT-00036 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-00031_VT-00037 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00031_VT-00038 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00031_VT-00039 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00031_VT-00040 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00031_VT-00041 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VGP-00021

### Gauge & Gauge Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Gauge & Gauge Controller Verification: Configuration

See 4.2 for generic configuration.

### Gauge & Gauge Controller Verification: Setup

See 4.3 for generic setup.

Gauge shall be under the nominal vacuum range before proceeding to the test.

Gauge shall be connected and shall not be measuring before starting the test.

Gauge controller shall be energized and shall not display any error to start the verification procedure.

A pre-calibrate simulator can be used instead of the gauge to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the gauge.

The GUI panel shall show that the gauge to be check is free of errors before starting the verification procedure.

### Gauge & Gauge Controller Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the gauge.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VGP-00021: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VGP-00021_CR.01 | LEBT-010:VAC-VGP-00021_MR.01 | LEBT-010:VAC-VGP-00021_DAR.01 | LEBT-010:VAC-VGP-00021_CsR.01 | LEBT-010:VAC-VEG-00011_SR.01 | LEBT-010:VAC-VEG-00011_IR.01 |
|  | LEBT-010:VAC-VGP-00021_MR.02 |  |  |  | LEBT-010:VAC-VEG-10001_IR.01 |
|  | LEBT-010:VAC-VGP-00021_MR.03 |  |  |  | LEBT-010:VAC-VEG-10010_IR.01 |
|  | LEBT-010:VAC-VGP-00021_MR.04 |  |  |  | LEBT-010:VAC-VEG-20020_IR.01 |
|  | LEBT-010:VAC-VGP-00021_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VGP-00021_MR.06 |  |  |  |  |
|  | LEBT-010:VAC-VGP-00021_MR.07 |  |  |  |  |
|  | LEBT-010:VAC-VGP-00021_MR.08 |  |  |  |  |
|  | LEBT-010:VAC-VGP-00021_MR.09 |  |  |  |  |
|  | LEBT-010:VAC-VGP-00021_MR.10 |  |  |  |  |
|  | LEBT-010:VAC-VGP-00021_MR.11 |  |  |  |  |

#### LEBT-010:VAC-VGP-00021: Procedure of verification

LEBT-010:VAC-VGP-00021_VT-00001: Gauge Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 27	LEBT-010:VAC-VGP-00021: Control & Monitoring (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGP-00021_VT-00002 | Assess the gauge “Off” status. | No action required because the gauge shall already be off. Off, the gauge shall display a pressure of 1000 mbar. | Assess the gauge “Off” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGP-00021_VT-00003 | Assess the gauge “On” status. | Stat the gauge. | Assess the “On” status of the gauge. | □ |
|  |  |  | Assess the “On” status of the gauge on the gauge controller. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGP-00021_VT-00004 | Verify the pressure archiving. | Open archiving appliance. | Assess the value of the archived pressure. | □ |
|  |  |  | Assess the consistency between the row value and the scaled value. | □ |
| LEBT-010:VAC-VGP-00021_VT-00005 | Verify the pressure archiving - Data Acquisition Alarm. | Disconnect or simulate a disconnection of the data acquisition analog measurement. | Assess the alarm on the control screen. | □ |

Table 28	LEBT-010:VAC-VGP-00021: Control & Monitoring (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGP-00021_VT-00006 | Verify the over-range status. | Create or simulate an over-range pressure to be read by the gauge. | Assess the gauge “Over-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGP-00021_VT-00007 | Verify the under-range status. | Create or simulate an under-range pressure to be read by the gauge. | Assess the gauge “Under-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGP-00021_VT-00008 | Verify that the parameters of the gauges can be remotely modified. | Choose a parameter relative to the gauge. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ____________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |
| LEBT-010:VAC-VGP-00021_VT-00009 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ___________ _________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |

## Test case LEBT-010:VAC-VPT-02100

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Configuration

See 4.2 for generic configuration.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Setup

See 4.3 for generic setup.

Turbo-molecular pump shall be connected and shall not be running before starting the test.

Turbo-molecular pump controller shall be energized and shall not display any error to start the verification procedure.

The GUI panel shall show that the controller to be check is free of errors before starting the verification procedure.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the pump.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VPT-02100: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VPT-02100_CR.01 | LEBT-010: VAC-VPT-02100_MR.01 | LEBT-010:VAC-VPT-02100_DAR.01 | LEBT-010:VAC-VPT-02100_CsR.01 | LEBT-010:VAC-VPT-02100_SR.01 | LEBT-010:VAC-VPT-02100_IR.01 |
| LEBT-010:VAC-VPT-02100_CR.02 | LEBT-010:VAC-VPT-02100_MR.02 | LEBT-010:VAC-VPT-02100_DAR.02 |  |  |  |
| LEBT-010:VAC-VPT-02100_CR.03 | LEBT-010:VAC-VPT-02100_MR.03 |  |  |  |  |
|  | LEBT-010:VAC-VPT-02100_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VPT-02100_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VPT-02100_MR.06 |  |  |  |  |

#### LEBT-010:VAC-VPT-02100: Procedure of verification

LEBT-010:VAC-VPT-02100_VT-00001: Pump Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 29	LEBT-010:VAC-VPT-02100: Remote Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-02100_VT-00002 | Verify the manual remote control of the pump. | Set “Manual” mode using the detailed GUI panel of the pump. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before starting the pump. | □ |
| LEBT-010:VAC-VPT-02100_VT-00003 | Verify the error status. | Ensure that the turbomolecular pump controller is not running and disconnect the turbomolecular pump cable. Start the pump. | Assess the “Error” status on the GUI panel. | □ |
|  |  |  | Assess the “Error” status on the turbomolecular pump controller: the LED “ERROR” is on. | □ |
| LEBT-010:VAC-VPT-02100_VT-00004 | Test the reset command. | After reconnecting the turbomolecular pump cable, reset the pump controller. | Assess that the “Error” status on the GUI panel disappears. | □ |
|  |  |  | Assess that the “Error” status on the turbomolecular pump controller disappear, the LED “ERROR” is off. | □ |
| LEBT-010:VAC-VPT-02100_VT-00005 | Start the turbomolecular pump remotely. | Start the turbomolecular pump. | Assess the “On” status on the GUI panel. Assess the “Accelerating” status on the GUI panel | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “STATUS” is on. | □ |
|  |  |  | Assess the accelerating status show by the LEDs “LOAD” on the turbomolecular pump controller. | □ |

Table 30	LEBT-010:VAC-VPT-02100: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-02100_VT-00006 | Assess turbomolecular pump controller parameters monitoring. | Assess evolution of dynamic parameters (converter frequency). | Control system monitors dynamic parameters. | □ |
| LEBT-010:VAC-VPT-02100_VT-00007 | Stop the turbomolecular pump remotely. | Stop the turbomolecular pump. | Assess the “Off” status. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: “STATUS” LED is off. | □ |
| LEBT-010:VAC-VPT-02100_VT-00008 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. | Write down the value of the parameter before the modification: ________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : ________________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: ________________________________________ | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 31		LEBT-010:VAC-VPT-02100: “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-02100_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPT-02100_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VPT-02100_VT-00009 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-02100_VT-00010 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-02100_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-02100_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-02100_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 32		LEBT-010:VAC-VPT-02100: “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-02100_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPT-02100_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  |  |
| LEBT-010:VAC-VPT-02100_VT-00016 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-02100_VT-00017 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-02100_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-02100_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-02100_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VVA-02100

### Angle Valves & Gates Valves Verification: Support Environment.

See 4.1 for generic support environment.

### Angle Valves & Gates Valves Verification: Configuration

See 4.2 for generic configuration.

### Angle Valves & Gates Valves Verification: Setup

See 4.3 for generic setup.

Angle valve or gate valve shall be connected and shall not be open before starting the test.

A simulator can be used instead of the valve to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the valve.

The GUI panel shall show that the valve to be check is free of errors before starting the verification procedure.

### Angle Valves & Gates Valves Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the valve.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VVA-02100: List of requirements

| Reference to the requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VVA-02100_CR.01 | LEBT-010:VAC-VVA-02100_MR.01 | LEBT-010:VAC-VVA-02100_DAR.01 | LEBT-010:VAC-VVA-02100_CsR.01 | LEBT-010:VAC-VVA-02100_SR.01 | LEBT-010:VAC-VVA-02100_IR.01 |
| LEBT-010:VAC-VVA-02100_CR.02 | LEBT-010:VAC-VVA-02100_MR.02 | LEBT-010:VAC-VVA-02100_DAR.02 |  |  |  |
|  | LEBT-010:VAC-VVA-02100_MR.03 | LEBT-010:VAC-VVA-02100_DAR.03 |  |  |  |
|  | LEBT-010:VAC-VVA-02100_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VVA-02100_MR.05 |  |  |  |  |

#### LEBT-010:VAC-VVA-02100: Procedure of verification

LEBT-010:VAC-VVA-02100_VT-00001: Valve Cable Number __________________________________________(Check cable labelling on both side of the cable).

Table 33	LEBT-010:VAC-VVA-02100: Remote & Manual Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-02100_VT-00002 | Assess the closed status of the valve. | No action required because the valve shall already be closed. | Assess the “Close” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-02100_VT-00003 | Assess the “Undefined” status of the valve. | Disconnect the control cable from the connector on the valve. Wait that “Undefined” time-out elapsed. | Assess the “Undefined” status on the GUI panel. | □ |

Table 34	LEBT-010:VAC-VVA-02100: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-02100_VT-00004 | Verify the manual remote control of the valve. | Set “Manual” mode using the detailed GUI panel of the valve. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before opening the valve. | □ |
| LEBT-010:VAC-VVA-02100_VT-00005 | Verify the opening function. | Verify that there are no active interlocks applied to the valve. Open the valve through the GUI panel. | Assess the “Open” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-02100_VT-00006 | Verify the closing function. | Close the valve through the GUI panel. | Assess the “Close” status on the GUI panel. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 35	LEBT-010:VAC-VVA-02100: First “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-02100_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-02100_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VGP-00021 (Relay 1) _____________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-02100_VT-00009 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-02100_VT-00010 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-02100_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-02100_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-02100_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 36	LEBT-010:VAC-VVA-02100: Second “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-02100_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-02100_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-02100_VT-00016 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-02100_VT-00017 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-02100_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-02100_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-02100_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 37	LEBT-010:VAC-VVA-02100: First “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-02100_VT-00021 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-02100_VT-00022 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-02100_VT-00023 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-02100_VT-00024 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-02100_VT-00025 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-02100_VT-00026 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-02100_VT-00027 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 38	LEBT-010:VAC-VVA-02100: Second “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-02100_VT-00028 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-02100_VT-00029 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VPT-02100 (Nominal Speed) _______________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-02100_VT-00030 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-02100_VT-00031 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-02100_VT-00032 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-02100_VT-00033 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-02100_VT-00034 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 39	LEBT-010:VAC-VVA-02100: Third “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-02100_VT-00035 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-02100_VT-00036 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-02100_VT-00037 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-02100_VT-00038 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-02100_VT-00039 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-02100_VT-00040 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-02100_VT-00041 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VPT-03100

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Configuration

See 4.2 for generic configuration.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Setup

See 4.3 for generic setup.

Turbo-molecular pump shall be connected and shall not be running before starting the test.

Turbo-molecular pump controller shall be energized and shall not display any error to start the verification procedure.

The GUI panel shall show that the controller to be check is free of errors before starting the verification procedure.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the pump.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VPT-03100: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VPT-03100_CR.01 | LEBT-010: VAC-VPT-03100_MR.01 | LEBT-010:VAC-VPT-03100_DAR.01 | LEBT-010:VAC-VPT-03100_CsR.01 | LEBT-010:VAC-VPT-03100_SR.01 | LEBT-010:VAC-VPT-03100_IR.01 |
| LEBT-010:VAC-VPT-03100_CR.02 | LEBT-010:VAC-VPT-03100_MR.02 | LEBT-010:VAC-VPT-03100_DAR.02 |  |  |  |
| LEBT-010:VAC-VPT-03100_CR.03 | LEBT-010:VAC-VPT-03100_MR.03 |  |  |  |  |
|  | LEBT-010:VAC-VPT-03100_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VPT-03100_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VPT-03100_MR.06 |  |  |  |  |

#### LEBT-010:VAC-VPT-03100: Procedure of verification

LEBT-010:VAC-VPT-03100_VT-00001: Pump Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 40	LEBT-010:VAC-VPT-03100: Remote Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-03100_VT-00002 | Verify the manual remote control of the pump. | Set “Manual” mode using the detailed GUI panel of the pump. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before starting the pump. | □ |
| LEBT-010:VAC-VPT-03100_VT-00003 | Verify the error status. | Ensure that the turbomolecular pump controller is not running and disconnect the turbomolecular pump cable. Start the pump. | Assess the “Error” status on the GUI panel. | □ |
|  |  |  | Assess the “Error” status on the turbomolecular pump controller: the LED “ERROR” is on. | □ |
| LEBT-010:VAC-VPT-03100_VT-00004 | Test the reset command. | After reconnecting the turbomolecular pump cable, reset the pump controller. | Assess that the “Error” status on the GUI panel disappears. | □ |
|  |  |  | Assess that the “Error” status on the turbomolecular pump controller disappear, the LED “ERROR” is off. | □ |
| LEBT-010:VAC-VPT-03100_VT-00005 | Start the turbomolecular pump remotely. | Start the turbomolecular pump. | Assess the “On” status on the GUI panel. Assess the “Accelerating” status on the GUI panel | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “STATUS” is on. | □ |
|  |  |  | Assess the accelerating status show by the LEDs “LOAD” on the turbomolecular pump controller. | □ |

Table 41	LEBT-010:VAC-VPT-03100: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-03100_VT-00006 | Assess turbomolecular pump controller parameters monitoring. | Assess evolution of dynamic parameters (converter frequency). | Control system monitors dynamic parameters. | □ |
| LEBT-010:VAC-VPT-03100_VT-00007 | Stop the turbomolecular pump remotely. | Stop the turbomolecular pump. | Assess the “Off” status. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: “STATUS” LED is off. | □ |
| LEBT-010:VAC-VPT-03100_VT-00008 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. | Write down the value of the parameter before the modification: ________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : ________________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: ________________________________________ | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 42		LEBT-010:VAC-VPT-03100: “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-03100_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPT-03100_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VPT-03100_VT-00009 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-03100_VT-00010 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-03100_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-03100_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-03100_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 43		LEBT-010:VAC-VPT-03100: “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-03100_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPT-03100_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  |  |
| LEBT-010:VAC-VPT-03100_VT-00016 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-03100_VT-00017 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-03100_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-03100_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-03100_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VVA-03100

### Angle Valves & Gates Valves Verification: Support Environment.

See 4.1 for generic support environment.

### Angle Valves & Gates Valves Verification: Configuration

See 4.2 for generic configuration.

### Angle Valves & Gates Valves Verification: Setup

See 4.3 for generic setup.

Angle valve or gate valve shall be connected and shall not be open before starting the test.

A simulator can be used instead of the valve to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the valve.

The GUI panel shall show that the valve to be check is free of errors before starting the verification procedure.

### Angle Valves & Gates Valves Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the valve.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VVA-03100: List of requirements

| Reference to the requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VVA-03100_CR.01 | LEBT-010:VAC-VVA-03100_MR.01 | LEBT-010:VAC-VVA-03100_DAR.01 | LEBT-010:VAC-VVA-03100_CsR.01 | LEBT-010:VAC-VVA-03100_SR.01 | LEBT-010:VAC-VVA-03100_IR.01 |
| LEBT-010:VAC-VVA-03100_CR.02 | LEBT-010:VAC-VVA-03100_MR.02 | LEBT-010:VAC-VVA-03100_DAR.02 |  |  |  |
|  | LEBT-010:VAC-VVA-03100_MR.03 | LEBT-010:VAC-VVA-03100_DAR.03 |  |  |  |
|  | LEBT-010:VAC-VVA-03100_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VVA-03100_MR.05 |  |  |  |  |

#### LEBT-010:VAC-VVA-03100: Procedure of verification

LEBT-010:VAC-VVA-03100_VT-00001: Valve Cable Number __________________________________________(Check cable labelling on both side of the cable).

Table 44	LEBT-010:VAC-VVA-03100: Remote & Manual Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-03100_VT-00002 | Assess the closed status of the valve. | No action required because the valve shall already be closed. | Assess the “Close” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-03100_VT-00003 | Assess the “Undefined” status of the valve. | Disconnect the control cable from the connector on the valve. Wait that “Undefined” time-out elapsed. | Assess the “Undefined” status on the GUI panel. | □ |

Table 45	LEBT-010:VAC-VVA-03100: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-03100_VT-00004 | Verify the manual remote control of the valve. | Set “Manual” mode using the detailed GUI panel of the valve. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before opening the valve. | □ |
| LEBT-010:VAC-VVA-03100_VT-00005 | Verify the opening function. | Verify that there are no active interlocks applied to the valve. Open the valve through the GUI panel. | Assess the “Open” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-03100_VT-00006 | Verify the closing function. | Close the valve through the GUI panel. | Assess the “Close” status on the GUI panel. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 46	LEBT-010:VAC-VVA-03100: First “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-03100_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-03100_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VGP-00021 (Relay 1) _____________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-03100_VT-00009 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-03100_VT-00010 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-03100_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-03100_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-03100_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 47	LEBT-010:VAC-VVA-03100: Second “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-03100_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-03100_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-03100_VT-00016 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-03100_VT-00017 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-03100_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-03100_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-03100_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 48	LEBT-010:VAC-VVA-03100: First “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-03100_VT-00021 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-03100_VT-00022 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-03100_VT-00023 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-03100_VT-00024 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-03100_VT-00025 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-03100_VT-00026 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-03100_VT-00027 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 49	LEBT-010:VAC-VVA-03100: Second “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-03100_VT-00028 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-03100_VT-00029 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VPT-03100 (Nominal Speed) _______________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-03100_VT-00030 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-03100_VT-00031 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-03100_VT-00032 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-03100_VT-00033 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-03100_VT-00034 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 50	LEBT-010:VAC-VVA-03100: Third “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-03100_VT-00035 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-03100_VT-00036 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-03100_VT-00037 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-03100_VT-00038 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-03100_VT-00039 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-03100_VT-00040 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-03100_VT-00041 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VGP-10000

### Gauge & Gauge Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Gauge & Gauge Controller Verification: Configuration

See 4.2 for generic configuration.

### Gauge & Gauge Controller Verification: Setup

See 4.3 for generic setup.

Gauge shall be under the nominal vacuum range before proceeding to the test.

Gauge shall be connected and shall not be measuring before starting the test.

Gauge controller shall be energized and shall not display any error to start the verification procedure.

A pre-calibrate simulator can be used instead of the gauge to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the gauge.

The GUI panel shall show that the gauge to be check is free of errors before starting the verification procedure.

### Gauge & Gauge Controller Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the gauge.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VGP-10000: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VGP-10000_CR.01 | LEBT-010:VAC-VGP-10000_MR.01 | LEBT-010:VAC-VGP-10000_DAR.01 | LEBT-010:VAC-VEG-10001_CsR.01 | LEBT-010:VAC-VEG-10001_SR.01 | LEBT-010:VAC-VEG-00011_IR.01 |
|  | LEBT-010:VAC-VGP-10000_MR.02 |  |  |  | LEBT-010:VAC-VEG-10001_IR.01 |
|  | LEBT-010:VAC-VGP-10000_MR.03 |  |  |  | LEBT-010:VAC-VEG-10010_IR.01 |
|  | LEBT-010:VAC-VGP-10000_MR.04 |  |  |  | LEBT-010:VAC-VEG-20020_IR.01 |
|  | LEBT-010:VAC-VGP-10000_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VGP-10000_MR.06 |  |  |  |  |
|  | LEBT-010:VAC-VGP-10000_MR.07 |  |  |  |  |
|  | LEBT-010:VAC-VGP-10000_MR.08 |  |  |  |  |
|  | LEBT-010:VAC-VGP-10000_MR.09 |  |  |  |  |
|  | LEBT-010:VAC-VGP-10000_MR.10 |  |  |  |  |
|  | LEBT-010:VAC-VGP-10000_MR.11 |  |  |  |  |

#### LEBT-010:VAC-VGP-10000: Procedure of verification

LEBT-010:VAC-VGP-10000_VT-00001: Gauge Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 51	LEBT-010:VAC-VGP-10000: Control & Monitoring (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGP-10000_VT-00002 | Assess the gauge “Off” status. | No action required because the gauge shall already be off. Off, the gauge shall display a pressure of 1000 mbar. | Assess the gauge “Off” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGP-10000_VT-00003 | Assess the gauge “On” status. | Stat the gauge. | Assess the “On” status of the gauge. | □ |
|  |  |  | Assess the “On” status of the gauge on the gauge controller. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGP-10000_VT-00004 | Verify the pressure archiving. | Open archiving appliance. | Assess the value of the archived pressure. | □ |
|  |  |  | Assess the consistency between the row value and the scaled value. | □ |
| LEBT-010:VAC-VGP-10000_VT-00005 | Verify the pressure archiving - Data Acquisition Alarm. | Disconnect or simulate a disconnection of the data acquisition analog measurement. | Assess the alarm on the control screen. | □ |

Table 52	LEBT-010:VAC-VGP-10000: Control & Monitoring (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGP-10000_VT-00006 | Verify the over-range status. | Create or simulate an over-range pressure to be read by the gauge. | Assess the gauge “Over-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGP-10000_VT-00007 | Verify the under-range status. | Create or simulate an under-range pressure to be read by the gauge. | Assess the gauge “Under-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGP-10000_VT-00008 | Verify that the parameters of the gauges can be remotely modified. | Choose a parameter relative to the gauge. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ____________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |
| LEBT-010:VAC-VGP-10000_VT-00009 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ___________ _________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |

## Test case LEBT-010:VAC-VGC-10000

### Gauge & Gauge Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Gauge & Gauge Controller Verification: Configuration

See 4.2 for generic configuration.

### Gauge & Gauge Controller Verification: Setup

See 4.3 for generic setup.

Gauge shall be under the nominal vacuum range before proceeding to the test.

Gauge shall be connected and shall not be measuring before starting the test.

Gauge controller shall be energized and shall not display any error to start the verification procedure.

A pre-calibrate simulator can be used instead of the gauge to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the gauge.

The GUI panel shall show that the gauge to be check is free of errors before starting the verification procedure.

### Gauge & Gauge Controller Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the gauge.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VGC-10000: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VGC-10000_CR.01 | LEBT-010:VAC-VGC-10000_MR.01 | LEBT-010:VAC-VGC-10000_DAR.01 | LEBT-010:VAC-VEG-10001_CsR.01 | LEBT-010:VAC-VEG-10001_SR.01 | LEBT-010:VAC-VEG-00011_IR.01 |
|  | LEBT-010:VAC-VGC-10000_MR.02 |  |  |  | LEBT-010:VAC-VEG-10001_IR.01 |
|  | LEBT-010:VAC-VGC-10000_MR.03 |  |  |  | LEBT-010:VAC-VEG-10010_IR.01 |
|  | LEBT-010:VAC-VGC-10000_MR.04 |  |  |  | LEBT-010:VAC-VEG-20020_IR.01 |
|  | LEBT-010:VAC-VGC-10000_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VGC-10000_MR.06 |  |  |  |  |
|  | LEBT-010:VAC-VGC-10000_MR.07 |  |  |  |  |
|  | LEBT-010:VAC-VGC-10000_MR.08 |  |  |  |  |
|  | LEBT-010:VAC-VGC-10000_MR.09 |  |  |  |  |
|  | LEBT-010:VAC-VGC-10000_MR.10 |  |  |  |  |
|  | LEBT-010:VAC-VGC-10000_MR.11 |  |  |  |  |

#### LEBT-010:VAC-VGC-10000: Procedure of verification

LEBT-010:VAC-VGC-10000_VT-00001: Gauge Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 53	LEBT-010:VAC-VGC-10000: Control & Monitoring (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGC-10000_VT-00002 | Assess the gauge “Off” status. | No action required because the gauge shall already be off. Off, the gauge shall display a pressure of 1000 mbar. | Assess the gauge “Off” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGC-10000_VT-00003 | Assess the gauge “On” status. | Stat the gauge. | Assess the “On” status of the gauge. | □ |
|  |  |  | Assess the “On” status of the gauge on the gauge controller. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGC-10000_VT-00004 | Verify the pressure archiving. | Open archiving appliance. | Assess the value of the archived pressure. | □ |
|  |  |  | Assess the consistency between the row value and the scaled value. | □ |
| LEBT-010:VAC-VGC-10000_VT-00005 | Verify the pressure archiving - Data Acquisition Alarm. | Disconnect or simulate a disconnection of the data acquisition analog measurement. | Assess the alarm on the control screen. | □ |

Table 54	LEBT-010:VAC-VGC-10000: Control & Monitoring (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGC-10000_VT-00006 | Verify the over-range status. | Create or simulate an over-range pressure to be read by the gauge. | Assess the gauge “Over-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGC-10000_VT-00007 | Verify the under-range status. | Create or simulate an under-range pressure to be read by the gauge. | Assess the gauge “Under-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGC-10000_VT-00008 | Verify that the parameters of the gauges can be remotely modified. | Choose a parameter relative to the gauge. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ____________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |
| LEBT-010:VAC-VGC-10000_VT-00009 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ___________ _________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |

## Test case LEBT-010:VAC-VGD-10000

### Gauge & Gauge Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Gauge & Gauge Controller Verification: Configuration

See 4.2 for generic configuration.

### Gauge & Gauge Controller Verification: Setup

See 4.3 for generic setup.

Gauge shall be under the nominal vacuum range before proceeding to the test.

Gauge shall be connected and shall not be measuring before starting the test.

Gauge controller shall be energized and shall not display any error to start the verification procedure.

A pre-calibrate simulator can be used instead of the gauge to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the gauge.

The GUI panel shall show that the gauge to be check is free of errors before starting the verification procedure.

### Gauge & Gauge Controller Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the gauge.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VGD-10000: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VGD-10000_CR.01 | LEBT-010:VAC-VGD-10000_MR.01 | LEBT-010:VAC-VGD-10000_DAR.01 | LEBT-010:VAC-VEVMC-10001_CsR.01 | LEBT-010:VAC-VEVMC-10001_SR.01 | LEBT-010:VAC- VEVMC -00011_IR.01 |
|  | LEBT-010:VAC-VGD-10000_MR.02 |  |  |  | LEBT-010:VAC- VEVMC -10001_IR.01 |
|  | LEBT-010:VAC-VGD-10000_MR.03 |  |  |  | LEBT-010:VAC- VEVMC -10010_IR.01 |
|  | LEBT-010:VAC-VGD-10000_MR.04 |  |  |  | LEBT-010:VAC- VEVMC -20020_IR.01 |
|  | LEBT-010:VAC-VGD-10000_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VGD-10000_MR.06 |  |  |  |  |
|  | LEBT-010:VAC-VGD-10000_MR.07 |  |  |  |  |
|  | LEBT-010:VAC-VGD-10000_MR.08 |  |  |  |  |
|  | LEBT-010:VAC-VGD-10000_MR.09 |  |  |  |  |
|  | LEBT-010:VAC-VGD-10000_MR.10 |  |  |  |  |
|  | LEBT-010:VAC-VGD-10000_MR.11 |  |  |  |  |

#### LEBT-010:VAC-VGD-10000: Procedure of verification

LEBT-010:VAC-VGD-10000_VT-00001: Gauge Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 55	LEBT-010:VAC-VGD-10000: Control & Monitoring (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGD-10000_VT-00002 | Assess the gauge “Off” status. | No action required because the gauge shall already be off. Off, the gauge shall display a pressure of 1000 mbar. | Assess the gauge “Off” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGD-10000_VT-00003 | Assess the gauge “On” status. | Stat the gauge. | Assess the “On” status of the gauge. | □ |
|  |  |  | Assess the “On” status of the gauge on the gauge controller. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGD-10000_VT-00004 | Verify the pressure archiving. | Open archiving appliance. | Assess the value of the archived pressure. | □ |
|  |  |  | Assess the consistency between the row value and the scaled value. | □ |
| LEBT-010:VAC-VGD-10000_VT-00005 | Verify the pressure archiving - Data Acquisition Alarm. | Disconnect or simulate a disconnection of the data acquisition analog measurement. | Assess the alarm on the control screen. | □ |

Table 56	LEBT-010:VAC-VGD-10000: Control & Monitoring (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGD-10000_VT-00006 | Verify the over-range status. | Create or simulate an over-range pressure to be read by the gauge. | Assess the gauge “Over-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGD-10000_VT-00007 | Verify the under-range status. | Create or simulate an under-range pressure to be read by the gauge. | Assess the gauge “Under-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGD-10000_VT-00008 | Verify that the parameters of the gauges can be remotely modified. | Choose a parameter relative to the gauge. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ____________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |
| LEBT-010:VAC-VGD-10000_VT-00009 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ___________ _________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |

## Test case LEBT-010:VAC-VPG-10001

### Vacuum Pumping Group Verification: Support Environment.

See 4.1 for generic support environment.

### Vacuum Pumping Group Verification: Configuration

See 4.2 for generic configuration.

### Vacuum Pumping Group Verification: Setup

See 4.3 for generic setup.

Devices that constitute the pumping group shall be tested and verified beforehand.

Adjacent pumping group, LEBT-010:VAC-VPG-20001, connected to the second sector shall be stopped to proceed to all of these test.

The GUI panel shall show that the devices to be check are free of errors before starting the verification procedure.

### Vacuum Pumping Group Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the device.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VPG-10001: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| No requirements | No requirements | No requirements | No requirements | LEBT-010:VAC-VEG-00011_SR.01 | No requirements |
|  |  |  |  | LEBT-010:VAC-VEG-00011_SR.02 |  |

#### LEBT-010:VAC-VPG-10001: Procedure of verification

Table 57	LEBT-010:VAC-VPG-10001: Pump-Down Atmospheric Pressure (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-10001_VT-00001 | Verify the pump down sequence (from atmospheric pressure). | Assess that the vacuum sector is at the atmospheric pressure. | Write down the actual pressure: _______________________________________ | □ |
|  |  | Set the “Normal” Mode. | Assess that it is not possible to start the pumping group. | □ |
|  |  |  | Assess the error. | □ |
|  |  | Disconnect the interlock from the gauge controller that conditions the starting of the turbomolecular pumps according to electrical diagram [6]. | Relay 1 of LEBT-010:VAC-VEG-00011 has been disconnected. | □ |
|  |  | Disconnect the open status of LEBT-010:VAC-VVA-00031 according to electrical diagram [6]. | Open status of LEBT-010:VAC-VVA-00031 is disconnected. | □ |
|  |  | Set the “Pump-Down” Mode. Reset the pumping group. | “Pump-Down” Mode is active. | □ |
|  |  |  | Assess that the error has disappeared. | □ |

Table 58	LEBT-010:VAC-VPG-10001: Pump-Down Atmospheric Pressure (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-10001_VT-00002 | Verify the pump down sequence (from atmospheric pressure). | Start the pumping group | Assess the opening of LEBT-010:VAC-VVA-00031. | □ |
|  |  |  | Assess the opening of LEBT-010:VAC-VVA-02100. | □ |
|  |  |  | Assess the opening of LEBT-010:VAC-VVA-03100. | □ |
|  |  |  | Assess the opening of ____-___:VAC-VVA-0__00. | □ |
|  |  |  | Assess the opening of ____-___:VAC-VVA-0__00. | □ |
|  |  |  | Assess the opening of ____-___:VAC-VVA-0__00. | □ |
|  |  |  | Assess the starting of the primary pump. | □ |
|  |  |  | Assess that turbomolecular pumps do not start. | □ |
|  |  | Wait that the delay has elapsed (more than 30s) | Assess that turbomolecular pumps do not start. | □ |
|  |  | Re-establish the interlock from the gauge controller that conditions the starting of the turbomolecular pumps according to electrical diagram [6]. | Assess that the turbomolecular pumps are starting. | □ |
|  |  | Pump down the vacuum sector. | Write down the pressure after having pumped down the sector: ___________________________ | □ |

Table 59	LEBT-010:VAC-VPG-10001: Normal Starting Sequence [sector under vacuum] (Part 1)

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-10001_VT-00003 | Verify the starting sequence (under vacuum). | Assess that the vacuum sector is under vacuum. | Write down the actual pressure: _______________________________________ | □ |
|  |  | Assess that the pumping group is stop. | All the pumps are off and the valves are close. | □ |
| LEBT-010:VAC-VPG-10001_VT-00004 | Disconnect the “interlocks” required by the sequences to progress (accordingly to the electrical diagram [6]). | Disconnect the interlock from the pump that conditions the opening of LEBT-010:VAC-VVA-00031. | Interlock has been disabled. | □ |
|  |  | Disconnect the interlock from the gauge controller that conditions the starting of the turbomolecular pumps. | Interlock has been disabled. | □ |
|  |  | Disconnect the interlock from the turbomolecular pump controller that conditions the opening of LEBT-010:VAC-VVA-02100. | Interlock has been disabled. | □ |
|  |  | Disconnect the interlock from the turbomolecular pump controller that conditions the opening of LEBT-010:VAC-VVA-03100. | Interlock has been disabled. | □ |
|  |  | Disconnect the interlock from the turbomolecular pump controller that conditions the opening of ____-___:VAC-VVA-0__00. | Interlock has been disabled. | □ |
|  |  | Disconnect the interlock from the turbomolecular pump controller that conditions the opening of ____-___:VAC-VVA-0__00. | Interlock has been disabled. | □ |
|  |  | Disconnect the interlock from the turbomolecular pump controller that conditions the opening of ____-___:VAC-VVA-0__00. | Interlock has been disabled. | □ |

Table 60	LEBT-010:VAC-VPG-10001: Normal Starting Sequence  [sector under vacuum] (Part 2)

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-10001_VT-00005 | Verify the starting sequence (under vacuum). | Start the pumping group. | Assess that the primary pump starts. | □ |
|  |  | Re-establish the interlock from the pump that conditions the opening of LEBT-010:VAC-VVA-00031. | Assess the opening of LEBT-010:VAC-VVA-00031. | □ |
|  |  | Re-establish disconnect the interlock from the gauge controller that conditions the starting of the turbomolecular pumps. | Assess the starting of the turbomolecular pumps. | □ |
|  |  | Once LEBT-010:VAC-VPT-02100 is at nominal speed, re-establish interlock from the turbomolecular pump controller that conditions the opening of LEBT-010:VAC-VVA-02100. | Assess the opening of LEBT-010:VAC-VVA-02100. | □ |
|  |  | Once LEBT-010:VAC-VPT-03100 is at nominal speed, re-establish interlock from the turbomolecular pump controller that conditions the opening of LEBT-010:VAC-VVA-03100. | Assess the opening of LEBT-010:VAC-VVA-03100. | □ |
|  |  | Once ____-___:VAC-VPT-0__00 is at nominal speed, re-establish interlock from the turbomolecular pump controller that conditions the opening of ____-___:VAC-VVA-0__00. | Assess the opening of ____-___:VAC-VVA-0__00. | □ |
|  |  | Once ____-___:VAC-VPT-0__00 is at nominal speed, re-establish interlock from the turbomolecular pump controller that conditions the opening of ____-___:VAC-VVA-0__00. | Assess the opening of ____-___:VAC-VVA-0__00. | □ |
|  |  | Once ____-___:VAC-VPT-0__00 is at nominal speed, re-establish interlock from the turbomolecular pump controller that conditions the opening of ____-___:VAC-VVA-0__00. | Assess the opening of ____-___:VAC-VVA-0__00. | □ |

Table 61	LEBT-010:VAC-VPG-10001: Normal Stopping Sequence [sector under vacuum] (Part 1)

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-10001_VT-00006 | Verify the stopping sequence (under vacuum). | Assess that the vacuum sector is under vacuum. | Write down the actual pressure: _______________________________________ | □ |
|  |  | Assess that the pumping group is running. | All the pumps are running and all the valves are open. | □ |
| LEBT-010:VAC-VPG-10001_VT-00007 | Disconnect valves close status. | Disconnect the close status of ____-___:VAC-VVA-0__00 according to electrical diagram [6]. | Close status of ____-___:VAC-VVA-0__00 is disconnected. | □ |
|  |  | Disconnect the close status of ____-___:VAC-VVA-0__00 according to electrical diagram [6]. | Close status of ____-___:VAC-VVA-0__00 is disconnected. | □ |
|  |  | Disconnect the close status of ____-___:VAC-VVA-0__00 according to electrical diagram [6]. | Close status of ____-___:VAC-VVA-0__00 is disconnected. | □ |
|  |  | Disconnect the close status of LEBT-010:VAC-VVA-03100 according to electrical diagram [6]. | Close status of LEBT-010:VAC-VVA-03100 is disconnected. | □ |
|  |  | Disconnect the close status of LEBT-010:VAC-VVA-02100 according to electrical diagram [6]. | Close status of LEBT-010:VAC-VVA-02100 is disconnected. | □ |
|  |  | Disconnect the close status of LEBT-010:VAC-VVA-00031 according to electrical diagram [6]. | Close status of LEBT-010:VAC-VVA-00031 is disconnected. | □ |

Table 62	LEBT-010:VAC-VPG-10001: Normal Stopping Sequence [sector under vacuum] (Part 2)

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-10001_VT-00008 | Verify the stopping sequence (under vacuum). | Stop the pumping group. | Assess that the valves on the turbomolecular pumps are closed in the tunnel. | □ |
|  |  |  | Assess that the turbomolecular pumps are still running. | □ |

Table 63	LEBT-010:VAC-VPG-10001: Normal Stopping Sequence [sector under vacuum] (Part 3)

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-10001_VT-00009 | Reconnect valves close status. | Reconnect the close status of ____-___:VAC-VVA-0__00 according to electrical diagram [6]. | Assess the close status of ____-___:VAC-VVA-0__00. | □ |
|  |  |  | Assess that ____-___:VAC-VPT-0__00 is stopping. | □ |
|  |  | Reconnect the close status of ____-___:VAC-VVA-0__00 according to electrical diagram [6]. | Assess the close status of ____-___:VAC-VVA-0__00. | □ |
|  |  |  | Assess that ____-___:VAC-VPT-0__00 is stopping. | □ |
|  |  | Reconnect the close status of ____-___:VAC-VVA-0__00 according to electrical diagram [6]. | Assess the close status of ____-___:VAC-VVA-0__00. | □ |
|  |  |  | Assess that ____-___:VAC-VPT-0__00 is stopping. | □ |
|  |  | Reconnect the close status of LEBT-010:VAC-VVA-03100 according to electrical diagram [6]. | Assess the close status of LEBT-010:VAC-VVA-03100. | □ |
|  |  |  | Assess that LEBT-010:VAC-VPT-03100 is stopping. | □ |
|  |  | Reconnect the close status of LEBT-010:VAC-VVA-02100 according to electrical diagram [6]. | Assess the close status of LEBT-010:VAC-VVA-02100. | □ |
|  |  |  | Assess that LEBT-010:VAC-VPT-02100 is stopping. | □ |
|  |  | Reconnect the close status of LEBT-010:VAC-VVA-00031 according to electrical diagram [6]. | Assess the close status of LEBT-010:VAC-VVA-00031. | □ |
|  |  |  | Assess that LEBT-010:VAC-VPDP-00031 is stopping. | □ |

Table 64	LEBT-010:VAC-VPG-10001: Maintenance (Leak Detection) Sequence.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-10001_VT-00010 | Verify the leak detection sequence (under vacuum). | Assess that the vacuum sector is under vacuum. | Write down the actual pressure: _______________________________________ | □ |
|  |  | Assess that a leak detector is connected to the sector and is running. | Write down the actual pressure of the leak detector: _______________________________________ | □ |
|  |  | Assess that the pumping group is running and the turbomolecular pump is/are running at the nominal speed. | Pumps are running and valves are open. | □ |
|  |  | Switch to the “Leak Detection” Mode. | “Leak Detection” Mode is active. | □ |
|  |  | Manually open or close the valve upon the primary pump. | The valve upon the primary pump is manually controlled. | □ |
|  |  | Switch back to the “Normal” Mode. | “Leak Detection” Mode is active. | □ |
|  |  |  | The valve upon the primary pump is no more manually controlled. | □ |

Table 65	LEBT-010:VAC-VPG-10001: Local Protections (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-10001_VT-00011 | Assess the configuration of the hardware interlock. | Asses that the hardware interlock has been configured. | The interlock is not configured. | □ |
|  |  |  | The interlock is configured. | □ |
|  | Hardware interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
|  | Verify that the tripped interlock stop the pumping group. | Start the pumping group and wait that it reaches its nominal state. Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess that the group stop. | □ |
| LEBT-010:VAC-VPG-10001_VT-00012 | Assess the configuration of the software interlock. | Asses that the hardware interlock has been configured. | The interlock is not configured. | □ |
|  |  |  | The interlock is configured. | □ |
|  | Software interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
|  | Verify that the tripped interlock stop the pumping group. | Start the pumping group and wait that it reaches its nominal state. Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess that the group stop. | □ |

Table 66	LEBT-010:VAC-VPG-10001: Local Protections (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-10001_VT-00013 | Turbo-Pumps Controller Error | Start the pumping group and wait that it reaches its nominal state. Simulate an error on the first turbomolecular pump controller according to the electrical diagram [6]: LEBT-010:VAC-VEPT-02100. | Assess that the pumping group stops. | □ |
|  |  |  | Assess that the pumping group keep pumping. | □ |
|  |  | Do not reset the pumping group. Simulate an error on the second turbomolecular pump controller according to the electrical diagram [6] : LEBT-010:VAC-VEPT-03100. | Assess that the pumping group stop. | □ |
|  |  |  | Assess that the pumping group keep pumping. | □ |
|  |  | Do not reset the pumping group. Simulate an error on the third turbomolecular pump controller according to the electrical diagram [6] : ____-___:VAC-VEPT-_____. | Assess that the pumping group stops. | □ |
|  |  |  | Assess that the pumping group keep pumping. | □ |
|  |  | Do not reset the pumping group. Simulate an error on the fourth turbomolecular pump controller according to the electrical diagram [6] : ____-___:VAC-VEPT-_____. | Assess that the pumping group stops. | □ |
|  |  |  | Assess that the pumping group keep pumping. | □ |
|  |  | Do not reset the pumping group. Simulate an error on the fifth turbomolecular pump controller according to the electrical diagram [6] : ____-___:VAC-VEPT-_____. | Assess that the pumping group stops. | □ |
|  |  |  | Assess that the pumping group keep pumping. | □ |
|  |  | Re-establish each of the simulated errors. Reset the pumping group. | Assess that there are no errors on the pumping group. | □ |
|  |  |  | Assess that there is no error on any of the turbomolecular pump controllers. |  |

Table 67	LEBT-010:VAC-VPG-10001: Local Protections (Part 3).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-10001_VT-00014 | Power Supply Error | Start the pumping group and wait that it reaches its nominal state. Trigger or simulate a power supply error according to the electrical diagram [6]. | Assess that the pumping group stops. | □ |
|  | Power Supply Error - Automatic restart. | If the automatic restart function is used and has been set, re-establish the power supply or remove the simulation of the error. | Assess that the error message disappear. | □ |
|  |  |  | Assess that the pumping group is restarting. | □ |
| LEBT-010:VAC-VPG-10001_VT-00015 | Max Auto-Restart (If the automatic restart function is used and has been set) | Start the pumping group and wait that it reaches its nominal state. Trigger or simulate a power supply error according to the electrical diagram [6]. | Assess that the pumping group stops. | □ |
|  |  | Re-establish the power supply or remove the simulation of the error. | Assess that the error message disappear. | □ |
|  |  |  | Assess that the pumping group is restarting. | □ |
|  |  | Trigger or simulate a power supply error according to the electrical diagram [6]. | Assess that the pumping group stops. | □ |
|  |  | Wait that the maximal mount of restart tentative has been reached. Re-establish the power supply or remove the simulation of the error and do not reset the pumping group. | Assess that the pumping group doesn’t restart. | □ |

Table 68	LEBT-010:VAC-VPG-10001: Local Protections (Part 4 - Pressure Interlock).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-10001_VT-00016 | High Vacuum Manifold Vented Error- Pressure Interlock. | Identify the source of the interlock (Device & Relay) according to the settings document [7]: ____________________________________________________________________________________________ |  | □ |
|  |  | Write down the setting of the threshold before the test [7]:______________________________________________ |  | □ |
|  |  | Start the pumping group and wait that it reaches its nominal state. Set a new (unreachable) set-point or switch off the gauge or simulate that the relay has tripped. | Write down the threshold set for the test: _______________________________________ | □ |
|  |  |  | Assess that the pumping group stops. | □ |
|  | High Vacuum Manifold Vented Error- Pressure Interlock. Automatic restart. | If the automatic restart function is used and has been set, re-establish the setting of the threshold or remove the simulation of the error. | Assess that the error message disappear. | □ |
|  |  |  | Assess that the pumping group is restarting. | □ |
| LEBT-010:VAC-VPG-10001_VT-00017 | Low Vacuum Manifold Vented Error - Pressure Interlock. | Identify the source of the interlock (Device & Relay) according to the settings document [7]: LEBT-010:VAC-VGP-00021 (Relay 1) _______________________________________________________________ |  | □ |
|  |  | Write down the setting of the threshold before the test [7]:______________________________________________ |  | □ |
|  |  | Start the pumping group and wait that it reaches its nominal state. Set a new (unreachable) set-point or switch off the gauge or simulate that the relay has tripped. | Write down the threshold set for the test: _______________________________________ | □ |
|  |  |  | Assess that the pumping group stops. | □ |
|  | Low Vacuum Manifold Vented Error - Pressure Interlock Automatic restart. | If the automatic restart function is used and has been set, re-establish the setting of the threshold or remove the simulation of the error. | Assess that the error message disappear. | □ |
|  |  |  | Assess that the pumping group is restarting. | □ |

Table 69	LEBT-010:VAC-VPG-10001: Local Protections (Part 5 - Pressure Interlock).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-10001_VT-00018 | Vacuum Sector Vented - Pressure Interlock. | Pumping group stopped in normal mode. Vent the system at the atmospheric pressure. | Write down the threshold used to assess atmospheric pressure: _______________________________________ | □ |
|  |  |  | When the atmospheric pressure is reached, assess that the error appears. | □ |
|  |  | Pumping group stopped in normal mode. Sector vented at atmospheric pressure. Switch the operation mode to “Pump-Down” and reset the pumping group. | Assess that the error has disappeared. | □ |

Table 70	LEBT-010:VAC-VPG-10001: Local Protections (Part 6).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-10001_VT-00019 | Primary Pump Error Case 1: Pumping group without back-up primary pump. | Start the pumping group and wait that it reaches its nominal state. Trigger or simulate an error on the primary pump controller according to the electrical diagram [6]. | Assess that the pumping group stops. | □ |
|  | Primary Pump Error Case 2: Pumping group with back-up primary pump. | Start the pumping group and wait that it reaches its nominal state. Trigger or simulate an error on the primary pump controller according to the electrical diagram [6]. | Assess that the primary pump is stopped. | □ |
|  |  |  | Assess that the valve upon the primary pump is closes. | □ |
|  |  |  | Assess that the pumping group keeps running. | □ |
| LEBT-010:VAC-VPG-10001_VT-00020 | Primary Pump / Valve Error Case 1: Pumping group without back-up primary pump. | Pumping group stopped; disconnect the digital output that controls the valve upon the primary pump according to the electrical diagram [6]. Start the pumping group, wait that the error delay’s has elapsed. | Assess that the primary pump starts. | □ |
|  |  |  | Assess that the valve remain close. | □ |
|  |  |  | Assess that the pumping group stops after the delay. | □ |
|  | Primary Pump / Valve Error Case 2: Pumping group with back-up primary pump. | Pumping group stopped; lock close the valve upon the primary pump. Start the pumping group. | Assess that the primary pump starts. | □ |
|  |  |  | Assess that the valve remain close. | □ |
|  |  |  | Assess that the bypass valve open and that the pumping group keep starting. | □ |

Table 71	LEBT-010:VAC-VPG-10001: Local Protections (Part 7).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-10001_VT-00021 | Turbo-Pumps Not Available | Pumping group stopped; lock off all the turbomolecular pumps controllers except one. | Only one turbomolecular pump controller has not been locked. | □ |
|  |  | Disconnect the digital input that read the nominal speed status of the non-locked turbomolecular pump controller according to the electrical diagram [6]. Start the pumping group. | Assess that the pumping group is starting. | □ |
|  |  | Once the turbomolecular pump controller has started, simulate an error. | Assess that the pumping group stops. | □ |

## Test case LEBT-010:VAC-VPM-00011

### Pressure Manometer Verification: Support Environment.

See 4.1 for generic support environment.

### Pressure Manometer Verification: Configuration

See 4.2 for generic configuration.

### Pressure Manometer Verification: Setup

See 4.3 for generic setup.

### Pressure Manometer Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the device.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VPM-00011: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VPM-00011_CR.01 | LEBT-010:VAC-VPM-00011_MR.01 | LEBT-010:VAC-VPM-00011_DAR.01 | LEBT-010:VAC-VPM-00011_CsR.01 | LEBT-010:VAC-VPM-00011_SR.01 | LEBT-010:VAC-VPM-00011_IR.01 |
|  | LEBT-010:VAC-VPM-00011_MR.02 |  |  |  |  |

#### LEBT-010:VAC-VPM-00011: Procedure of verification

LEBT-010:VAC-VPM-00011_VT-00001: Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 72	LEBT-010:VAC-VPM-00011: Control & Monitoring.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPM-00011_VT-00002 | Assess the pressure value. | Read pressure on the GUI panel. | Assess the pressure on the GUI panel. | □ |
|  |  |  | Corroborate the pressure on the GUI panel with the pressure display on the monometer. | □ |
| LEBT-010:VAC-VPM-00011_VT-00003 | Verify the pressure archiving. | Open archiving appliance. | Assess the value of the archived pressure. | □ |
| LEBT-010:VAC-VPM-00011_VT-00004 | Test the low pressure alarm. | Create or simulate a drop-down of the pressure read by the pressure manometer. | Assess that the alarm is active on the control room. | □ |
|  |  | It is also possible to modify the alarm threshold. | Write down the initial threshold before modification: _______________________________________ | □ |
|  |  |  | Write down the threshold set for the test: _______________________________________ | □ |
|  |  |  | Assess that the alarm is active on the control room. | □ |
|  |  |  | Write down value set after the test: ______________________________________ | □ |

## Test case LEBT-010:VAC-VVA-01100

### Angle Valves & Gates Valves Verification: Support Environment.

See 4.1 for generic support environment.

### Angle Valves & Gates Valves Verification: Configuration

See 4.2 for generic configuration.

### Angle Valves & Gates Valves Verification: Setup

See 4.3 for generic setup.

Angle valve or gate valve shall be connected and shall not be open before starting the test.

A simulator can be used instead of the valve to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the valve.

The GUI panel shall show that the valve to be check is free of errors before starting the verification procedure.

### Angle Valves & Gates Valves Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the valve.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VVA-01100: List of requirements

| Reference to the requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VVA-01100_CR.01 | LEBT-010:VAC-VVA-01100_MR.01 | LEBT-010:VAC-VVA-01100_DAR.01 | LEBT-010:VAC-VVA-01100_CsR.01 | LEBT-010:VAC-VVA-01100_SR.01 | LEBT-010:VAC-VVA-01100_IR.01 |
| LEBT-010:VAC-VVA-01100_CR.02 | LEBT-010:VAC-VVA-01100_MR.02 | LEBT-010:VAC-VVA-01100_DAR.02 |  | LEBT-010:VAC-VEG-1001_SR.01 |  |
| LEBT-010:VAC-VVA-01100_CR.03 | LEBT-010:VAC-VVA-01100_MR.03 | LEBT-010:VAC-VVA-01100_DAR.03 |  |  |  |
|  | LEBT-010:VAC-VVA-01100_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VVA-01100_MR.05 |  |  |  |  |

#### LEBT-010:VAC-VVA-01100: Procedure of verification

LEBT-010:VAC-VVA-01100_VT-00001: Pump Cable Number __________________________________________(Check cable labelling on both side of the cable).

Table 73		LEBT-010:VAC-VVA-01100: Remote & Manual Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-01100_VT-00002 | Assess the closed status of the valve. | No action required because the valve shall already be closed. | Assess the “Close” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-01100_VT-00003 | Assess the “Undefined” status of the valve. | Disconnect the control cable from the connector on the valve. Wait that “Undefined” time-out elapsed. | Assess the “Undefined” status on the GUI panel. | □ |

Table 74		LEBT-010:VAC-VVA-01100: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-01100_VT-00004 | Verify the manual remote control of the valve. | Set “Manual” mode using the detailed GUI panel of the valve. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before opening the valve. | □ |
| LEBT-010:VAC-VVA-01100_VT-00005 | Verify the opening function. | Verify that there are no active interlocks applied to the valve. Open the valve through the GUI panel. | Assess the “Open” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-01100_VT-00006 | Verify the closing function. | Close the valve through the GUI panel. | Assess the “Close” status on the GUI panel. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 75		LEBT-010:VAC-VVA-01100: First “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-01100_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-01100_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VGC-10000 (Relay 11) ____________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-01100_VT-00009 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-01100_VT-00010 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-01100_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-01100_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-01100_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 76		LEBT-010:VAC-VVA-01100: Second “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-01100_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-01100_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-01100_VT-00016 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-01100_VT-00017 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-01100_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-01100_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-01100_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 77	LEBT-010:VAC-VVA-01100: First “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-01100_VT-00021 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-01100_VT-00022 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-01100_VT-00023 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-01100_VT-00024 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-01100_VT-00025 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-01100_VT-00026 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-01100_VT-00027 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 78	LEBT-010:VAC-VVA-01100: Second “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-01100_VT-00028 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-01100_VT-00029 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-01100_VT-00030 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-01100_VT-00031 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-01100_VT-00032 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-01100_VT-00033 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-01100_VT-00034 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 79	LEBT-010:VAC-VVA-01100: Third “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-01100_VT-00035 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-01100_VT-00036 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-01100_VT-00037 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-01100_VT-00038 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-01100_VT-00039 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-01100_VT-00040 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-01100_VT-00041 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

Table 80	LEBT-010:VAC-VVA-01100: Access Interlock (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-01100_VT-00042 | Verify the closure of the valve in case of access of person in the tunnel. | Start the vacuum system and set the nominal conditions to produce beam. Open the valve. | Assess that the valve is open. | □ |
|  |  | Request an access to the MCR or simulate it according to the electrical diagram [6]. | Assess that the valve closes. | □ |

## Test case LEBT-010:VAC-VVMC-01100

### Mass Flow Meter & Mass Flow Meter Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Mass Flow Meter & Mass Flow Meter Controller Verification: Configuration

See 4.2 for generic configuration.

### Mass Flow Meter & Mass Flow Meter Controller Verification: Setup

See 4.3 for generic setup.

Mass flow meter shall be under the nominal vacuum range before proceeding to the test.

Mass flow meter shall be connected and shall be close before starting the test.

Mass flow meter controller shall be energized and shall not display any error to start the verification procedure.

### Mass Flow Meter & Mass Flow Meter Controller Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the mass flow meter.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VVMC-01100: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VVMC-01100_CR.01 | LEBT-010:VAC-VVMC-01100_MR.01 | LEBT-010:VAC-VVMC-01100_DAR.01 | LEBT-010:VAC-VEVMC-01100_CsR.01 | LEBT-010:VAC-VEVMC-01100_SR.01 | LEBT-010:VAC-VEVMC-01100_IR.01 |
|  | LEBT-010:VAC-VVMC-01100_MR.02 |  | LEBT-010:VAC-VEVMC-02200_CsR.01 | LEBT-010:VAC-VEVMC-02200_SR.01 | LEBT-010:VAC-VEVMC-02200_IR.01 |
|  | LEBT-010:VAC-VVMC-01100_MR.03 |  | LEBT-010:VAC-VEVMC-10001_CsR.01 | LEBT-010:VAC-VEVMC-10001_SR.01 | LEBT-010:VAC-VEVMC-10001_IR.01 |
|  | LEBT-010:VAC-VVMC-01100_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VVMC-01100_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VVMC-01100_MR.06 |  |  |  |  |
|  | LEBT-010:VAC-VVMC-01100_MR.07 |  |  |  |  |
|  | LEBT-010:VAC-VVMC-01100_MR.08 |  |  |  |  |
|  | LEBT-010:VAC-VVMC-01100_MR.09 |  |  |  |  |
|  | LEBT-010:VAC-VVMC-01100_MR.10 |  |  |  |  |
|  | LEBT-010:VAC-VVMC-01100_MR.11 |  |  |  |  |

#### LEBT-010:VAC-VVMC-01100: Procedure of verification

LEBT-010:VAC-VVMC-01100_VT-00001: Pump Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 81	LEBT-010:VAC-VVMC-01100: Control & Monitoring (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVMC-01100_VT-00002 | Assess the partial opening. | Partially open the mass flow meter through the GUI panel. | Assess the partial opening on the GUI panel. | □ |
|  |  |  | Assess the partial opening on the mass flow meter controller | □ |
| LEBT-010:VAC-VVMC-01100_VT-00003 | Assess the partial closing. | Partially close the mass flow meter through the GUI panel. | Assess the partial closing on the GUI panel. | □ |
|  |  |  | Assess the partial closing on the mass flow meter controller | □ |

Table 82	LEBT-010:VAC-VVMC-01100: Control & Monitoring (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVMC-01100_VT-00004 | Verify that the parameters of the mass flow meter can be remotely modified. | Choose a parameter relative to the gauge. | Write down the value of the parameter before the modification: ________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : ________________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: ________________________________________ | □ |
| LEBT-010:VAC-VVMC-01100_VT-00005 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. | Write down the value of the parameter before the modification: ________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : ________________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: ________________________________________ | □ |

## Test case LEBT-010:VAC-VGR-10000

### Residual Gas Analyzer & Residual Gas Analyzer Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Residual Gas Analyzer & Residual Gas Analyzer Controller Verification: Configuration

See 4.2 for generic configuration.

### Residual Gas Analyzer & Residual Gas Analyzer Controller Verification: Setup

See 4.3 for generic setup.

Residual gas analyzer shall be under the nominal vacuum range before proceeding to the test.

Residual gas analyzer shall be connected and shall not be measuring before starting the test.

Residual gas analyzer controller shall be energized and shall not display any error to start the verification procedure.

### Residual Gas Analyzer & Residual Gas Analyzer Controller Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the device.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VGR-10000: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VGR-10000_CR.01 | LEBT-010:VAC-VGR-10000_MR.01 | LEBT-010:VAC-VGR-10000_DAR.01 | LEBT-010:VAC-VGR-10000_CsR.01 | LEBT-010:VAC- VGR-10000_SR.01 | LEBT-010:VAC- VGR-10000_IR.01 |
|  | LEBT-010:VAC-VGR-10000_MR.02 |  |  | LEBT-010:VAC- VGR-10000_SR.02 |  |
|  | LEBT-010:VAC-VGR-10000_MR.03 |  |  |  |  |

#### LEBT-010:VAC-VGR-10000: Procedure of verification

LEBT-010:VAC-VGR-10000_VT-00001: Pump Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 83	LEBT-010:VAC-VGR-10000: Control & Monitoring.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGR-10000_VT-00002 | Assess the remote control of the residual gas analyser. | Start residual gas analyser through the GUI panel. | Read feedback gas analysis. | □ |
| LEBT-010:VAC-VGR-10000_VT-00003 | Verify the pressure interlock of the residual gas analyser. | Identify the source of the interlock (Device & Relay) according to the settings document [7]: _________________________________________________________________________________________ |  | □ |
|  |  | Write down the setting of the threshold before the test [7]:________________________________________ |  | □ |
|  |  | Set a new (unreachable) set-point or switch off the gauge or simulate that the relay has tripped. | Write down the threshold set for the test: _______________________________________ | □ |
|  |  |  | Assess that the residual gas analyser stops. | □ |

# Test Cases “LEBT-010:VAC" (Second Vacuum Sector)

## Test case LEBT-010:VAC-VPDP-00071

### Primary Pump & Primary Pump Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Primary Pump & Primary Pump Controller Verification: Configuration

See 4.2 for generic configuration.

### Primary Pump & Primary Pump Controller Verification: Setup

See 4.3 for generic setup.

Primary pump shall be connected and shall not be running before starting the test.

Primary pump controller shall be energized, shall not display any error and control switch shall be on “PLC” position to start the verification procedure.

The GUI panel shall show that the controller to be check is free of errors before starting the verification procedure.

### Primary Pump & Primary Pump Controller Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the pump.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VPDP-00071: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VPDP-00071_CR.01 | LEBT-010:VAC-VPDP-00071_MR.01 | LEBT-010:VAC-VPDP-00071_DAR.01 | LEBT-010:VAC-VPDP-00071_CsR.01 | LEBT-010:VAC-VPDP-00071_SR.01 | LEBT-010:VAC-VPDP-00071_IR.01 |
| LEBT-010:VAC-VPDP-00071_CR.02 | LEBT-010:VAC-VPDP-00071_MR.02 |  |  |  |  |
| LEBT-010:VAC-VPDP-00071_CR.03 | LEBT-010:VAC-VPDP-00071_MR.03 |  |  |  |  |
| LEBT-010:VAC-VPDP-00071_CR.04 | LEBT-010:VAC-VPDP-00071_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VPDP-00071_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VPDP-00071_MR.06 |  |  |  |  |

#### LEBT-010:VAC-VPDP-00071: Procedure of verification

LEBT-010:VAC-VPDP-00071_VT-00001: Pump Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 84		LEBT-010:VAC-VPDP-00071: Local Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPDP-00071_VT-00002 | Control the pump disconnection protection. | On the tunnel, after having verified that the pump is not running, disconnect the power supply connector. | Assess the corresponding error on the GUI panel: “Pump Not Connected”. | □ |
|  |  |  | Assess the corresponding error on the primary pump controller: the LED “Cable Connected” is off. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00003 | Reset the pump disconnected error. | After having assessed the disconnected error, reconnect the power supply connector. Reset the error from the GUI. | Assess that the “Pump Not Connected” error has disappeared on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Cable Connected” is on. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00004 | Assess the “Local Control” status. | Actuate the “Control” switch to the “Local” position on the primary pump controller. | Assess the “Local” Status on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Local Control” is on. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00005 | Start the pump by the primary pump controller. | Make sure that the system is in a safe condition before starting the pump. | Assess that the system is in a safe condition to start the pump. | □ |
|  |  | Actuate the “Control” switch to the “ON” position on the primary pump controller. | Verify that the pump in running on the tunnel. | □ |
|  |  |  | Assess the “On” status on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Pump ON” is on. | □ |

Table 85		LEBT-010:VAC-VPDP-00071: Local Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPDP-00071_VT-00006 | Stop the pump by the primary pump controller. | Actuate the “Control” switch to the “OFF” position on the primary pump controller. | Assess the “Off” status on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Pump ON” is off. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00007 | Verify the error status. | Open primary pump controller crate and trip the circuit breaker. Close primary pump controller crate. Actuate “Control” switch to the “ON” position on the primary pump controller. Wait error timeout. | Assess the “CB Fail” status on the GUI panel. | □ |
|  |  |  | Assess the “Error” status on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Error” is on. | □ |
|  |  |  | Actuate the “Control” switch to the “OFF” position on the primary pump controller. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00008 | Eliminate the previous error. | Actuate “Control” switch to the “OFF” position on the primary pump controller. Open primary pump controller crate, close the circuit breaker and close primary pump controller crate. | Circuit breaker is healthy and the “Error” LED is on. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00009 | Reset the pump error (remotely). | Reset the error from the GUI. | Assess that the “Error” and “CB Fail” status has disappeared on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Error” is off. | □ |

Table 86		LEBT-010:VAC-VPDP-00071: Local Control (Part 3).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPDP-00071_VT-00010 | Verify the “Remote” status. | Actuate the “Control” switch to the “PLC” position on the primary pump controller. | Assess the “Remote” status on the GUI panel: “Local” status shall have disappeared. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “PLC Control” is on and the LED “Local Control” is off. | □ |

Table 87		LEBT-010:VAC-VPDP-00071: Remote Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPDP-00071_VT-00011 | Verify the manual remote control of the pump. | Set “Manual” mode using the detailed GUI panel of the pump. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before starting the pump. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00012 | Start the primary pump remotely. | Start the primary pump through the GUI command | Assess the “On” status on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Pump ON” is on. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00013 | Stop the primary pump remotely. | Stop the primary pump through the GUI command | Assess the “Off” status on the GUI panel. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “Pump ON” is off. | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 88		LEBT-010:VAC-VPDP-00071: “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPDP-00071_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VPDP-00071_VT-00009 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00010 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 89		LEBT-010:VAC-VPDP-00071: “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPDP-00071_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  |  |
| LEBT-010:VAC-VPDP-00071_VT-00016 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00017 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPDP-00071_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VVA-00071

### Angle Valves & Gates Valves Verification: Support Environment.

See 4.1 for generic support environment.

### Angle Valves & Gates Valves Verification: Configuration

See 4.2 for generic configuration.

### Angle Valves & Gates Valves Verification: Setup

See 4.3 for generic setup.

Angle valve or gate valve shall be connected and shall not be open before starting the test.

A simulator can be used instead of the valve to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the valve.

The GUI panel shall show that the valve to be check is free of errors before starting the verification procedure.

### Angle Valves & Gates Valves Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the valve.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VVA-00071: List of requirements

| Reference to the requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VVA-00071_CR.01 | LEBT-010:VAC-VVA-00071_MR.01 | LEBT-010:VAC-VVA-00071_DAR.01 | LEBT-010:VAC-VVA-00071_CsR.01 | LEBT-010:VAC-VVA-00071_SR.01 | LEBT-010:VAC-VVA-00071_IR.01 |
| LEBT-010:VAC-VVA-00071_CR.02 | LEBT-010:VAC-VVA-00071_MR.02 | LEBT-010:VAC-VVA-00071_DAR.02 |  |  |  |
|  | LEBT-010:VAC-VVA-00071_MR.03 | LEBT-010:VAC-VVA-00071_DAR.03 |  |  |  |
|  | LEBT-010:VAC-VVA-00071_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VVA-00071_MR.05 |  |  |  |  |

#### LEBT-010:VAC-VVA-00071: Procedure of verification

LEBT-010:VAC-VVA-00071_VT-00001: Valve Cable Number __________________________________________(Check cable labelling on both side of the cable).

Table 90		LEBT-010:VAC-VVA-00071: Remote & Manual Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00071_VT-00002 | Assess the closed status of the valve. | No action required because the valve shall already be closed. | Assess the “Close” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-00071_VT-00003 | Assess the “Undefined” status of the valve. | Disconnect the control cable from the connector on the valve. Wait that “Undefined” time-out elapsed. | Assess the “Undefined” status on the GUI panel. | □ |

Table 91		LEBT-010:VAC-VVA-00071: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00071_VT-00004 | Verify the manual remote control of the valve. | Set “Manual” mode using the detailed GUI panel of the valve. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before opening the valve. | □ |
| LEBT-010:VAC-VVA-00071_VT-00005 | Verify the opening function. | Verify that there are no active interlocks applied to the valve. Open the valve through the GUI panel. | Assess the “Open” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-00071_VT-00006 | Verify the closing function. | Close the valve through the GUI panel. | Assess the “Close” status on the GUI panel. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 92		LEBT-010:VAC-VVA-00071: First “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00071_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-00071_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-00071_VT-00009 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00071_VT-00010 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00071_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00071_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00071_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 93		LEBT-010:VAC-VVA-00071: Second “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00071_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-00071_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VGP-00081 (Relay 3) _____________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-00071_VT-00016 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00071_VT-00017 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00071_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00071_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00071_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 94	LEBT-010:VAC-VVA-00071: First “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00071_VT-00021 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-00071_VT-00022 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-VAC:VPDP-00071 (Nominal Speed) _____________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-00071_VT-00023 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00071_VT-00024 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00071_VT-00025 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00071_VT-00026 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00071_VT-00027 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 95	LEBT-010:VAC-VVA-00071: Second “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00071_VT-00028 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-00071_VT-00029 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-00071_VT-00030 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00071_VT-00031 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00071_VT-00032 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00071_VT-00033 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00071_VT-00034 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 96	LEBT-010:VAC-VVA-00071: Third “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00071_VT-00035 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-00071_VT-00036 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-00071_VT-00037 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00071_VT-00038 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00071_VT-00039 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00071_VT-00040 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00071_VT-00041 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VGP-00081

### Gauge & Gauge Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Gauge & Gauge Controller Verification: Configuration

See 4.2 for generic configuration.

### Gauge & Gauge Controller Verification: Setup

See 4.3 for generic setup.

Gauge shall be under the nominal vacuum range before proceeding to the test.

Gauge shall be connected and shall not be measuring before starting the test.

Gauge controller shall be energized and shall not display any error to start the verification procedure.

A pre-calibrate simulator can be used instead of the gauge to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the gauge.

The GUI panel shall show that the gauge to be check is free of errors before starting the verification procedure.

### Gauge & Gauge Controller Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the gauge.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VGP-00081: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VGP-00081_CR.01 | LEBT-010:VAC-VGP-00081_MR.01 | LEBT-010:VAC-VGP-00081_DAR.01 | LEBT-010:VAC-VGP-00081_CsR.01 | LEBT-010:VAC-VEG-00011_SR.01 | LEBT-010:VAC-VEG-00011_IR.01 |
|  | LEBT-010:VAC-VGP-00081_MR.02 |  |  |  | LEBT-010:VAC-VEG-10001_IR.01 |
|  | LEBT-010:VAC-VGP-00081_MR.03 |  |  |  | LEBT-010:VAC-VEG-10010_IR.01 |
|  | LEBT-010:VAC-VGP-00081_MR.04 |  |  |  | LEBT-010:VAC-VEG-20020_IR.01 |
|  | LEBT-010:VAC-VGP-00081_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VGP-00081_MR.06 |  |  |  |  |
|  | LEBT-010:VAC-VGP-00081_MR.07 |  |  |  |  |
|  | LEBT-010:VAC-VGP-00081_MR.08 |  |  |  |  |
|  | LEBT-010:VAC-VGP-00081_MR.09 |  |  |  |  |
|  | LEBT-010:VAC-VGP-00081_MR.10 |  |  |  |  |
|  | LEBT-010:VAC-VGP-00081_MR.11 |  |  |  |  |

#### LEBT-010:VAC-VGP-00081: Procedure of verification

LEBT-010:VAC-VGP-00081_VT-00001: Gauge Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 97	LEBT-010:VAC-VGP-00081: Control & Monitoring (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGP-00081_VT-00002 | Assess the gauge “Off” status. | No action required because the gauge shall already be off. Off, the gauge shall display a pressure of 1000 mbar. | Assess the gauge “Off” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGP-00081_VT-00003 | Assess the gauge “On” status. | Stat the gauge. | Assess the “On” status of the gauge. | □ |
|  |  |  | Assess the “On” status of the gauge on the gauge controller. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGP-00081_VT-00004 | Verify the pressure archiving. | Open archiving appliance. | Assess the value of the archived pressure. | □ |
|  |  |  | Assess the consistency between the row value and the scaled value. | □ |
| LEBT-010:VAC-VGP-00081_VT-00005 | Verify the pressure archiving - Data Acquisition Alarm. | Disconnect or simulate a disconnection of the data acquisition analog measurement. | Assess the alarm on the control screen. | □ |

Table 98	LEBT-010:VAC-VGP-00081: Control & Monitoring (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGP-00081_VT-00006 | Verify the over-range status. | Create or simulate an over-range pressure to be read by the gauge. | Assess the gauge “Over-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGP-00081_VT-00007 | Verify the under-range status. | Create or simulate an under-range pressure to be read by the gauge. | Assess the gauge “Under-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGP-00081_VT-00008 | Verify that the parameters of the gauges can be remotely modified. | Choose a parameter relative to the gauge. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ____________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |
| LEBT-010:VAC-VGP-00081_VT-00009 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ___________ _________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |

## Test case LEBT-010:VAC-VPT-06100

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Configuration

See 4.2 for generic configuration.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Setup

See 4.3 for generic setup.

Turbo-molecular pump shall be connected and shall not be running before starting the test.

Turbo-molecular pump controller shall be energized and shall not display any error to start the verification procedure.

The GUI panel shall show that the controller to be check is free of errors before starting the verification procedure.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the pump.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VPT-06100: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VPT-06100_CR.01 | LEBT-010: VAC-VPT-06100_MR.01 | LEBT-010:VAC-VPT-06100_DAR.01 | LEBT-010:VAC-VPT-06100_CsR.01 | LEBT-010:VAC-VPT-06100_SR.01 | LEBT-010:VAC-VPT-06100_IR.01 |
| LEBT-010:VAC-VPT-06100_CR.02 | LEBT-010:VAC-VPT-06100_MR.02 | LEBT-010:VAC-VPT-06100_DAR.02 |  |  |  |
| LEBT-010:VAC-VPT-06100_CR.03 | LEBT-010:VAC-VPT-06100_MR.03 |  |  |  |  |
|  | LEBT-010:VAC-VPT-06100_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VPT-06100_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VPT-06100_MR.06 |  |  |  |  |

#### LEBT-010:VAC-VPT-06100: Procedure of verification

LEBT-010:VAC-VPT-06100_VT-00001: Pump Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 99	LEBT-010:VAC-VPT-06100: Remote Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-06100_VT-00002 | Verify the manual remote control of the pump. | Set “Manual” mode using the detailed GUI panel of the pump. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before starting the pump. | □ |
| LEBT-010:VAC-VPT-06100_VT-00003 | Verify the error status. | Ensure that the turbomolecular pump controller is not running and disconnect the turbomolecular pump cable. Start the pump. | Assess the “Error” status on the GUI panel. | □ |
|  |  |  | Assess the “Error” status on the turbomolecular pump controller: the LED “ERROR” is on. | □ |
| LEBT-010:VAC-VPT-06100_VT-00004 | Test the reset command. | After reconnecting the turbomolecular pump cable, reset the pump controller. | Assess that the “Error” status on the GUI panel disappears. | □ |
|  |  |  | Assess that the “Error” status on the turbomolecular pump controller disappear, the LED “ERROR” is off. | □ |
| LEBT-010:VAC-VPT-06100_VT-00005 | Start the turbomolecular pump remotely. | Start the turbomolecular pump. | Assess the “On” status on the GUI panel. Assess the “Accelerating” status on the GUI panel | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “STATUS” is on. | □ |
|  |  |  | Assess the accelerating status show by the LEDs “LOAD” on the turbomolecular pump controller. | □ |

Table 100	LEBT-010:VAC-VPT-06100: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-06100_VT-00006 | Assess turbomolecular pump controller parameters monitoring. | Assess evolution of dynamic parameters (converter frequency). | Control system monitors dynamic parameters. | □ |
| LEBT-010:VAC-VPT-06100_VT-00007 | Stop the turbomolecular pump remotely. | Stop the turbomolecular pump. | Assess the “Off” status. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: “STATUS” LED is off. | □ |
| LEBT-010:VAC-VPT-06100_VT-00008 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. | Write down the value of the parameter before the modification: ________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : ________________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: ________________________________________ | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 101		LEBT-010:VAC-VPT-06100: “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-06100_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPT-06100_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VPT-06100_VT-00009 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-06100_VT-00010 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-06100_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-06100_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-06100_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 102		LEBT-010:VAC-VPT-06100: “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-06100_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPT-06100_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  |  |
| LEBT-010:VAC-VPT-06100_VT-00016 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-06100_VT-00017 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-06100_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-06100_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-06100_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VVA-06100

### Angle Valves & Gates Valves Verification: Support Environment.

See 4.1 for generic support environment.

### Angle Valves & Gates Valves Verification: Configuration

See 4.2 for generic configuration.

### Angle Valves & Gates Valves Verification: Setup

See 4.3 for generic setup.

Angle valve or gate valve shall be connected and shall not be open before starting the test.

A simulator can be used instead of the valve to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the valve.

The GUI panel shall show that the valve to be check is free of errors before starting the verification procedure.

### Angle Valves & Gates Valves Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the valve.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VVA-06100: List of requirements

| Reference to the requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VVA-06100_CR.01 | LEBT-010:VAC-VVA-06100_MR.01 | LEBT-010:VAC-VVA-06100_DAR.01 | LEBT-010:VAC-VVA-06100_CsR.01 | LEBT-010:VAC-VVA-06100_SR.01 | LEBT-010:VAC-VVA-06100_IR.01 |
| LEBT-010:VAC-VVA-06100_CR.02 | LEBT-010:VAC-VVA-06100_MR.02 | LEBT-010:VAC-VVA-06100_DAR.02 |  |  |  |
|  | LEBT-010:VAC-VVA-06100_MR.03 | LEBT-010:VAC-VVA-06100_DAR.03 |  |  |  |
|  | LEBT-010:VAC-VVA-06100_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VVA-06100_MR.05 |  |  |  |  |

#### LEBT-010:VAC-VVA-06100: Procedure of verification

LEBT-010:VAC-VVA-06100_VT-00001: Valve Cable Number __________________________________________(Check cable labelling on both side of the cable).

Table 103	LEBT-010:VAC-VVA-06100: Remote & Manual Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-06100_VT-00002 | Assess the closed status of the valve. | No action required because the valve shall already be closed. | Assess the “Close” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-06100_VT-00003 | Assess the “Undefined” status of the valve. | Disconnect the control cable from the connector on the valve. Wait that “Undefined” time-out elapsed. | Assess the “Undefined” status on the GUI panel. | □ |

Table 104	LEBT-010:VAC-VVA-06100: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-06100_VT-00004 | Verify the manual remote control of the valve. | Set “Manual” mode using the detailed GUI panel of the valve. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before opening the valve. | □ |
| LEBT-010:VAC-VVA-06100_VT-00005 | Verify the opening function. | Verify that there are no active interlocks applied to the valve. Open the valve through the GUI panel. | Assess the “Open” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-06100_VT-00006 | Verify the closing function. | Close the valve through the GUI panel. | Assess the “Close” status on the GUI panel. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 105	LEBT-010:VAC-VVA-06100: First “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-06100_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-06100_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VGP-00081 (Relay 3) _____________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-06100_VT-00009 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-06100_VT-00010 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-06100_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-06100_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-06100_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 106	LEBT-010:VAC-VVA-06100: Second “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-06100_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-06100_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-06100_VT-00016 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-06100_VT-00017 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-06100_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-06100_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-06100_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 107	LEBT-010:VAC-VVA-06100: First “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-06100_VT-00021 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-06100_VT-00022 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-06100_VT-00023 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-06100_VT-00024 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-06100_VT-00025 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-06100_VT-00026 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-06100_VT-00027 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 108	LEBT-010:VAC-VVA-06100: Second “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-06100_VT-00028 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-06100_VT-00029 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VPT-06100 (Nominal Speed) _______________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-06100_VT-00030 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-06100_VT-00031 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-06100_VT-00032 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-06100_VT-00033 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-06100_VT-00034 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 109	LEBT-010:VAC-VVA-06100: Third “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-06100_VT-00035 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-06100_VT-00036 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-06100_VT-00037 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-06100_VT-00038 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-06100_VT-00039 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-06100_VT-00040 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-06100_VT-00041 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VPT-07100

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Configuration

See 4.2 for generic configuration.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Setup

See 4.3 for generic setup.

Turbo-molecular pump shall be connected and shall not be running before starting the test.

Turbo-molecular pump controller shall be energized and shall not display any error to start the verification procedure.

The GUI panel shall show that the controller to be check is free of errors before starting the verification procedure.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the pump.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VPT-07100: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VPT-07100_CR.01 | LEBT-010: VAC-VPT-07100_MR.01 | LEBT-010:VAC-VPT-07100_DAR.01 | LEBT-010:VAC-VPT-07100_CsR.01 | LEBT-010:VAC-VPT-07100_SR.01 | LEBT-010:VAC-VPT-07100_IR.01 |
| LEBT-010:VAC-VPT-07100_CR.02 | LEBT-010:VAC-VPT-07100_MR.02 | LEBT-010:VAC-VPT-07100_DAR.02 |  |  |  |
| LEBT-010:VAC-VPT-07100_CR.03 | LEBT-010:VAC-VPT-07100_MR.03 |  |  |  |  |
|  | LEBT-010:VAC-VPT-07100_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VPT-07100_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VPT-07100_MR.06 |  |  |  |  |

#### LEBT-010:VAC-VPT-07100: Procedure of verification

LEBT-010:VAC-VPT-07100_VT-00001: Pump Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 110	LEBT-010:VAC-VPT-07100: Remote Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-07100_VT-00002 | Verify the manual remote control of the pump. | Set “Manual” mode using the detailed GUI panel of the pump. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before starting the pump. | □ |
| LEBT-010:VAC-VPT-07100_VT-00003 | Verify the error status. | Ensure that the turbomolecular pump controller is not running and disconnect the turbomolecular pump cable. Start the pump. | Assess the “Error” status on the GUI panel. | □ |
|  |  |  | Assess the “Error” status on the turbomolecular pump controller: the LED “ERROR” is on. | □ |
| LEBT-010:VAC-VPT-07100_VT-00004 | Test the reset command. | After reconnecting the turbomolecular pump cable, reset the pump controller. | Assess that the “Error” status on the GUI panel disappears. | □ |
|  |  |  | Assess that the “Error” status on the turbomolecular pump controller disappear, the LED “ERROR” is off. | □ |
| LEBT-010:VAC-VPT-07100_VT-00005 | Start the turbomolecular pump remotely. | Start the turbomolecular pump. | Assess the “On” status on the GUI panel. Assess the “Accelerating” status on the GUI panel | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “STATUS” is on. | □ |
|  |  |  | Assess the accelerating status show by the LEDs “LOAD” on the turbomolecular pump controller. | □ |

Table 111	LEBT-010:VAC-VPT-07100: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-07100_VT-00006 | Assess turbomolecular pump controller parameters monitoring. | Assess evolution of dynamic parameters (converter frequency). | Control system monitors dynamic parameters. | □ |
| LEBT-010:VAC-VPT-07100_VT-00007 | Stop the turbomolecular pump remotely. | Stop the turbomolecular pump. | Assess the “Off” status. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: “STATUS” LED is off. | □ |
| LEBT-010:VAC-VPT-07100_VT-00008 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. | Write down the value of the parameter before the modification: ________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : ________________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: ________________________________________ | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 112		LEBT-010:VAC-VPT-07100: “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-07100_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPT-07100_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VPT-07100_VT-00009 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-07100_VT-00010 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-07100_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-07100_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-07100_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 113		LEBT-010:VAC-VPT-07100: “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-07100_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPT-07100_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  |  |
| LEBT-010:VAC-VPT-07100_VT-00016 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-07100_VT-00017 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-07100_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-07100_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-07100_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VVA-07100

### Angle Valves & Gates Valves Verification: Support Environment.

See 4.1 for generic support environment.

### Angle Valves & Gates Valves Verification: Configuration

See 4.2 for generic configuration.

### Angle Valves & Gates Valves Verification: Setup

See 4.3 for generic setup.

Angle valve or gate valve shall be connected and shall not be open before starting the test.

A simulator can be used instead of the valve to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the valve.

The GUI panel shall show that the valve to be check is free of errors before starting the verification procedure.

### Angle Valves & Gates Valves Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the valve.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VVA-07100: List of requirements

| Reference to the requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VVA-07100_CR.01 | LEBT-010:VAC-VVA-07100_MR.01 | LEBT-010:VAC-VVA-07100_DAR.01 | LEBT-010:VAC-VVA-07100_CsR.01 | LEBT-010:VAC-VVA-07100_SR.01 | LEBT-010:VAC-VVA-07100_IR.01 |
| LEBT-010:VAC-VVA-07100_CR.02 | LEBT-010:VAC-VVA-07100_MR.02 | LEBT-010:VAC-VVA-07100_DAR.02 |  |  |  |
|  | LEBT-010:VAC-VVA-07100_MR.03 | LEBT-010:VAC-VVA-07100_DAR.03 |  |  |  |
|  | LEBT-010:VAC-VVA-07100_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VVA-07100_MR.05 |  |  |  |  |

#### LEBT-010:VAC-VVA-07100: Procedure of verification

LEBT-010:VAC-VVA-07100_VT-00001: Valve Cable Number __________________________________________(Check cable labelling on both side of the cable).

Table 114	LEBT-010:VAC-VVA-07100: Remote & Manual Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-07100_VT-00002 | Assess the closed status of the valve. | No action required because the valve shall already be closed. | Assess the “Close” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-07100_VT-00003 | Assess the “Undefined” status of the valve. | Disconnect the control cable from the connector on the valve. Wait that “Undefined” time-out elapsed. | Assess the “Undefined” status on the GUI panel. | □ |

Table 115	LEBT-010:VAC-VVA-07100: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-07100_VT-00004 | Verify the manual remote control of the valve. | Set “Manual” mode using the detailed GUI panel of the valve. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before opening the valve. | □ |
| LEBT-010:VAC-VVA-07100_VT-00005 | Verify the opening function. | Verify that there are no active interlocks applied to the valve. Open the valve through the GUI panel. | Assess the “Open” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-07100_VT-00006 | Verify the closing function. | Close the valve through the GUI panel. | Assess the “Close” status on the GUI panel. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 116	LEBT-010:VAC-VVA-07100: First “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-07100_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-07100_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VGP-00081 (Relay 3) _____________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-07100_VT-00009 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-07100_VT-00010 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-07100_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-07100_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-07100_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 117	LEBT-010:VAC-VVA-07100: Second “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-07100_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-07100_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-07100_VT-00016 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-07100_VT-00017 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-07100_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-07100_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-07100_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 118	LEBT-010:VAC-VVA-07100: First “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-07100_VT-00021 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-07100_VT-00022 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-07100_VT-00023 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-07100_VT-00024 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-07100_VT-00025 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-07100_VT-00026 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-07100_VT-00027 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 119	LEBT-010:VAC-VVA-07100: Second “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-07100_VT-00028 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-07100_VT-00029 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VPT-07100 (Nominal Speed) _______________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-07100_VT-00030 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-07100_VT-00031 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-07100_VT-00032 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-07100_VT-00033 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-07100_VT-00034 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 120	LEBT-010:VAC-VVA-07100: Third “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-07100_VT-00035 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-07100_VT-00036 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-07100_VT-00037 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-07100_VT-00038 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-07100_VT-00039 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-07100_VT-00040 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-07100_VT-00041 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VGP-30000

### Gauge & Gauge Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Gauge & Gauge Controller Verification: Configuration

See 4.2 for generic configuration.

### Gauge & Gauge Controller Verification: Setup

See 4.3 for generic setup.

Gauge shall be under the nominal vacuum range before proceeding to the test.

Gauge shall be connected and shall not be measuring before starting the test.

Gauge controller shall be energized and shall not display any error to start the verification procedure.

A pre-calibrate simulator can be used instead of the gauge to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the gauge.

The GUI panel shall show that the gauge to be check is free of errors before starting the verification procedure.

### Gauge & Gauge Controller Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the gauge.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VGP-30000: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VGP-30000_CR.01 | LEBT-010:VAC-VGP-30000_MR.01 | LEBT-010:VAC-VGP-30000_DAR.01 | LEBT-010:VAC-VEG-10001_CsR.01 | LEBT-010:VAC-VEG-10001_SR.01 | LEBT-010:VAC-VEG-00011_IR.01 |
|  | LEBT-010:VAC-VGP-30000_MR.02 |  |  |  | LEBT-010:VAC-VEG-10001_IR.01 |
|  | LEBT-010:VAC-VGP-30000_MR.03 |  |  |  | LEBT-010:VAC-VEG-10010_IR.01 |
|  | LEBT-010:VAC-VGP-30000_MR.04 |  |  |  | LEBT-010:VAC-VEG-20020_IR.01 |
|  | LEBT-010:VAC-VGP-30000_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VGP-30000_MR.06 |  |  |  |  |
|  | LEBT-010:VAC-VGP-30000_MR.07 |  |  |  |  |
|  | LEBT-010:VAC-VGP-30000_MR.08 |  |  |  |  |
|  | LEBT-010:VAC-VGP-30000_MR.09 |  |  |  |  |
|  | LEBT-010:VAC-VGP-30000_MR.10 |  |  |  |  |
|  | LEBT-010:VAC-VGP-30000_MR.11 |  |  |  |  |

#### LEBT-010:VAC-VGP-30000: Procedure of verification

LEBT-010:VAC-VGP-30000_VT-00001: Gauge Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 121	LEBT-010:VAC-VGP-30000: Control & Monitoring (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGP-30000_VT-00002 | Assess the gauge “Off” status. | No action required because the gauge shall already be off. Off, the gauge shall display a pressure of 1000 mbar. | Assess the gauge “Off” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGP-30000_VT-00003 | Assess the gauge “On” status. | Stat the gauge. | Assess the “On” status of the gauge. | □ |
|  |  |  | Assess the “On” status of the gauge on the gauge controller. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGP-30000_VT-00004 | Verify the pressure archiving. | Open archiving appliance. | Assess the value of the archived pressure. | □ |
|  |  |  | Assess the consistency between the row value and the scaled value. | □ |
| LEBT-010:VAC-VGP-30000_VT-00005 | Verify the pressure archiving - Data Acquisition Alarm. | Disconnect or simulate a disconnection of the data acquisition analog measurement. | Assess the alarm on the control screen. | □ |

Table 122	LEBT-010:VAC-VGP-30000: Control & Monitoring (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGP-30000_VT-00006 | Verify the over-range status. | Create or simulate an over-range pressure to be read by the gauge. | Assess the gauge “Over-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGP-30000_VT-00007 | Verify the under-range status. | Create or simulate an under-range pressure to be read by the gauge. | Assess the gauge “Under-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGP-30000_VT-00008 | Verify that the parameters of the gauges can be remotely modified. | Choose a parameter relative to the gauge. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ____________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |
| LEBT-010:VAC-VGP-30000_VT-00009 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ___________ _________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |

## Test case LEBT-010:VAC-VGC-30000

### Gauge & Gauge Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Gauge & Gauge Controller Verification: Configuration

See 4.2 for generic configuration.

### Gauge & Gauge Controller Verification: Setup

See 4.3 for generic setup.

Gauge shall be under the nominal vacuum range before proceeding to the test.

Gauge shall be connected and shall not be measuring before starting the test.

Gauge controller shall be energized and shall not display any error to start the verification procedure.

A pre-calibrate simulator can be used instead of the gauge to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the gauge.

The GUI panel shall show that the gauge to be check is free of errors before starting the verification procedure.

### Gauge & Gauge Controller Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the gauge.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VGC-30000: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VGC-30000_CR.01 | LEBT-010:VAC-VGC-30000_MR.01 | LEBT-010:VAC-VGC-30000_DAR.01 | LEBT-010:VAC-VEG-10001_CsR.01 | LEBT-010:VAC-VEG-10001_SR.01 | LEBT-010:VAC-VEG-00011_IR.01 |
|  | LEBT-010:VAC-VGC-30000_MR.02 |  |  |  | LEBT-010:VAC-VEG-10001_IR.01 |
|  | LEBT-010:VAC-VGC-30000_MR.03 |  |  |  | LEBT-010:VAC-VEG-10010_IR.01 |
|  | LEBT-010:VAC-VGC-30000_MR.04 |  |  |  | LEBT-010:VAC-VEG-20020_IR.01 |
|  | LEBT-010:VAC-VGC-30000_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VGC-30000_MR.06 |  |  |  |  |
|  | LEBT-010:VAC-VGC-30000_MR.07 |  |  |  |  |
|  | LEBT-010:VAC-VGC-30000_MR.08 |  |  |  |  |
|  | LEBT-010:VAC-VGC-30000_MR.09 |  |  |  |  |
|  | LEBT-010:VAC-VGC-30000_MR.10 |  |  |  |  |
|  | LEBT-010:VAC-VGC-30000_MR.11 |  |  |  |  |

#### LEBT-010:VAC-VGC-30000: Procedure of verification

LEBT-010:VAC-VGC-30000_VT-00001: Gauge Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 123	LEBT-010:VAC-VGC-30000: Control & Monitoring (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGC-30000_VT-00002 | Assess the gauge “Off” status. | No action required because the gauge shall already be off. Off, the gauge shall display a pressure of 1000 mbar. | Assess the gauge “Off” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGC-30000_VT-00003 | Assess the gauge “On” status. | Stat the gauge. | Assess the “On” status of the gauge. | □ |
|  |  |  | Assess the “On” status of the gauge on the gauge controller. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGC-30000_VT-00004 | Verify the pressure archiving. | Open archiving appliance. | Assess the value of the archived pressure. | □ |
|  |  |  | Assess the consistency between the row value and the scaled value. | □ |
| LEBT-010:VAC-VGC-30000_VT-00005 | Verify the pressure archiving - Data Acquisition Alarm. | Disconnect or simulate a disconnection of the data acquisition analog measurement. | Assess the alarm on the control screen. | □ |

Table 124	LEBT-010:VAC-VGC-30000: Control & Monitoring (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGC-30000_VT-00006 | Verify the over-range status. | Create or simulate an over-range pressure to be read by the gauge. | Assess the gauge “Over-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGC-30000_VT-00007 | Verify the under-range status. | Create or simulate an under-range pressure to be read by the gauge. | Assess the gauge “Under-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGC-30000_VT-00008 | Verify that the parameters of the gauges can be remotely modified. | Choose a parameter relative to the gauge. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ____________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |
| LEBT-010:VAC-VGC-30000_VT-00009 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ___________ _________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |

## Test case LEBT-010:VAC-VPT-99998

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Configuration

See 4.2 for generic configuration.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Setup

See 4.3 for generic setup.

Turbo-molecular pump shall be connected and shall not be running before starting the test.

Turbo-molecular pump controller shall be energized and shall not display any error to start the verification procedure.

The GUI panel shall show that the controller to be check is free of errors before starting the verification procedure.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the pump.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VPT-99998: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VPT-06100_CR.01 | LEBT-010: VAC-VPT-06100_MR.01 | LEBT-010:VAC-VPT-06100_DAR.01 | LEBT-010:VAC-VPT-06100_CsR.01 | LEBT-010:VAC-VPT-06100_SR.01 | LEBT-010:VAC-VPT-06100_IR.01 |
| LEBT-010:VAC-VPT-06100_CR.02 | LEBT-010:VAC-VPT-06100_MR.02 | LEBT-010:VAC-VPT-06100_DAR.02 |  |  |  |
| LEBT-010:VAC-VPT-06100_CR.03 | LEBT-010:VAC-VPT-06100_MR.03 |  |  |  |  |
|  | LEBT-010:VAC-VPT-06100_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VPT-06100_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VPT-06100_MR.06 |  |  |  |  |

#### LEBT-010:VAC-VPT-99998: Procedure of verification

LEBT-010:VAC-VPT-99998_VT-00001: Pump Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 125	LEBT-010:VAC-VPT-99998: Remote Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-99998_VT-00002 | Verify the manual remote control of the pump. | Set “Manual” mode using the detailed GUI panel of the pump. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before starting the pump. | □ |
| LEBT-010:VAC-VPT-99998_VT-00003 | Verify the error status. | Ensure that the turbomolecular pump controller is not running and disconnect the turbomolecular pump cable. Start the pump. | Assess the “Error” status on the GUI panel. | □ |
|  |  |  | Assess the “Error” status on the turbomolecular pump controller: the LED “ERROR” is on. | □ |
| LEBT-010:VAC-VPT-99998_VT-00004 | Test the reset command. | After reconnecting the turbomolecular pump cable, reset the pump controller. | Assess that the “Error” status on the GUI panel disappears. | □ |
|  |  |  | Assess that the “Error” status on the turbomolecular pump controller disappear, the LED “ERROR” is off. | □ |
| LEBT-010:VAC-VPT-99998_VT-00005 | Start the turbomolecular pump remotely. | Start the turbomolecular pump. | Assess the “On” status on the GUI panel. Assess the “Accelerating” status on the GUI panel | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “STATUS” is on. | □ |
|  |  |  | Assess the accelerating status show by the LEDs “LOAD” on the turbomolecular pump controller. | □ |

Table 126	LEBT-010:VAC-VPT-99998: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-99998_VT-00006 | Assess turbomolecular pump controller parameters monitoring. | Assess evolution of dynamic parameters (converter frequency). | Control system monitors dynamic parameters. | □ |
| LEBT-010:VAC-VPT-99998_VT-00007 | Stop the turbomolecular pump remotely. | Stop the turbomolecular pump. | Assess the “Off” status. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: “STATUS” LED is off. | □ |
| LEBT-010:VAC-VPT-99998_VT-00008 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. | Write down the value of the parameter before the modification: ________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : ________________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: ________________________________________ | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 127		LEBT-010:VAC-VPT-99998: “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-99998_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPT-99998_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VPT-99998_VT-00009 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-99998_VT-00010 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-99998_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-99998_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-99998_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 128		LEBT-010:VAC-VPT-99998: “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-99998_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPT-99998_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  |  |
| LEBT-010:VAC-VPT-99998_VT-00016 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-99998_VT-00017 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-99998_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-99998_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-99998_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VVA-99998

### Angle Valves & Gates Valves Verification: Support Environment.

See 4.1 for generic support environment.

### Angle Valves & Gates Valves Verification: Configuration

See 4.2 for generic configuration.

### Angle Valves & Gates Valves Verification: Setup

See 4.3 for generic setup.

Angle valve or gate valve shall be connected and shall not be open before starting the test.

A simulator can be used instead of the valve to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the valve.

The GUI panel shall show that the valve to be check is free of errors before starting the verification procedure.

### Angle Valves & Gates Valves Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the valve.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VVA-99998: List of requirements

| Reference to the requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VVA-06100_CR.01 | LEBT-010:VAC-VVA-06100_MR.01 | LEBT-010:VAC-VVA-06100_DAR.01 | LEBT-010:VAC-VVA-06100_CsR.01 | LEBT-010:VAC-VVA-06100_SR.01 | LEBT-010:VAC-VVA-06100_IR.01 |
| LEBT-010:VAC-VVA-06100_CR.02 | LEBT-010:VAC-VVA-06100_MR.02 | LEBT-010:VAC-VVA-06100_DAR.02 |  |  |  |
|  | LEBT-010:VAC-VVA-06100_MR.03 | LEBT-010:VAC-VVA-06100_DAR.03 |  |  |  |
|  | LEBT-010:VAC-VVA-06100_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VVA-06100_MR.05 |  |  |  |  |

#### LEBT-010:VAC-VVA-99998: Procedure of verification

LEBT-010:VAC-VVA-99998_VT-00001: Valve Cable Number __________________________________________(Check cable labelling on both side of the cable).

Table 129	LEBT-010:VAC-VVA-99998: Remote & Manual Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-99998_VT-00002 | Assess the closed status of the valve. | No action required because the valve shall already be closed. | Assess the “Close” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-99998_VT-00003 | Assess the “Undefined” status of the valve. | Disconnect the control cable from the connector on the valve. Wait that “Undefined” time-out elapsed. | Assess the “Undefined” status on the GUI panel. | □ |

Table 130	LEBT-010:VAC-VVA-99998: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-99998_VT-00004 | Verify the manual remote control of the valve. | Set “Manual” mode using the detailed GUI panel of the valve. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before opening the valve. | □ |
| LEBT-010:VAC-VVA-99998_VT-00005 | Verify the opening function. | Verify that there are no active interlocks applied to the valve. Open the valve through the GUI panel. | Assess the “Open” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-99998_VT-00006 | Verify the closing function. | Close the valve through the GUI panel. | Assess the “Close” status on the GUI panel. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 131	LEBT-010:VAC-VVA-99998: First “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-99998_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-99998_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VGP-00081 (Relay 3) _____________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-99998_VT-00009 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99998_VT-00010 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99998_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99998_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99998_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 132	LEBT-010:VAC-VVA-99998: Second “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-99998_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-99998_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-99998_VT-00016 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99998_VT-00017 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99998_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99998_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99998_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 133	LEBT-010:VAC-VVA-99998: First “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-99998_VT-00021 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-99998_VT-00022 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-99998_VT-00023 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99998_VT-00024 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99998_VT-00025 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99998_VT-00026 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99998_VT-00027 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 134	LEBT-010:VAC-VVA-99998: Second “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-99998_VT-00028 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-99998_VT-00029 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VPT-99998 (Nominal Speed) _______________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-99998_VT-00030 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99998_VT-00031 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99998_VT-00032 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99998_VT-00033 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99998_VT-00034 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 135	LEBT-010:VAC-VVA-99998: Third “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-99998_VT-00035 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-99998_VT-00036 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-99998_VT-00037 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99998_VT-00038 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99998_VT-00039 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99998_VT-00040 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99998_VT-00041 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VPT-99999

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Configuration

See 4.2 for generic configuration.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Setup

See 4.3 for generic setup.

Turbo-molecular pump shall be connected and shall not be running before starting the test.

Turbo-molecular pump controller shall be energized and shall not display any error to start the verification procedure.

The GUI panel shall show that the controller to be check is free of errors before starting the verification procedure.

### Turbo-Molecular Pump & Turbo-Molecular Pump Controller Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the pump.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VPT-99999: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VPT-07100_CR.01 | LEBT-010: VAC-VPT-07100_MR.01 | LEBT-010:VAC-VPT-07100_DAR.01 | LEBT-010:VAC-VPT-07100_CsR.01 | LEBT-010:VAC-VPT-07100_SR.01 | LEBT-010:VAC-VPT-07100_IR.01 |
| LEBT-010:VAC-VPT-07100_CR.02 | LEBT-010:VAC-VPT-07100_MR.02 | LEBT-010:VAC-VPT-07100_DAR.02 |  |  |  |
| LEBT-010:VAC-VPT-07100_CR.03 | LEBT-010:VAC-VPT-07100_MR.03 |  |  |  |  |
|  | LEBT-010:VAC-VPT-07100_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VPT-07100_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VPT-07100_MR.06 |  |  |  |  |

#### LEBT-010:VAC-VPT-99999: Procedure of verification

LEBT-010:VAC-VPT-99999_VT-00001: Pump Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 136	LEBT-010:VAC-VPT-99999: Remote Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-99999_VT-00002 | Verify the manual remote control of the pump. | Set “Manual” mode using the detailed GUI panel of the pump. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before starting the pump. | □ |
| LEBT-010:VAC-VPT-99999_VT-00003 | Verify the error status. | Ensure that the turbomolecular pump controller is not running and disconnect the turbomolecular pump cable. Start the pump. | Assess the “Error” status on the GUI panel. | □ |
|  |  |  | Assess the “Error” status on the turbomolecular pump controller: the LED “ERROR” is on. | □ |
| LEBT-010:VAC-VPT-99999_VT-00004 | Test the reset command. | After reconnecting the turbomolecular pump cable, reset the pump controller. | Assess that the “Error” status on the GUI panel disappears. | □ |
|  |  |  | Assess that the “Error” status on the turbomolecular pump controller disappear, the LED “ERROR” is off. | □ |
| LEBT-010:VAC-VPT-99999_VT-00005 | Start the turbomolecular pump remotely. | Start the turbomolecular pump. | Assess the “On” status on the GUI panel. Assess the “Accelerating” status on the GUI panel | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: the LED “STATUS” is on. | □ |
|  |  |  | Assess the accelerating status show by the LEDs “LOAD” on the turbomolecular pump controller. | □ |

Table 137	LEBT-010:VAC-VPT-99999: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-99999_VT-00006 | Assess turbomolecular pump controller parameters monitoring. | Assess evolution of dynamic parameters (converter frequency). | Control system monitors dynamic parameters. | □ |
| LEBT-010:VAC-VPT-99999_VT-00007 | Stop the turbomolecular pump remotely. | Stop the turbomolecular pump. | Assess the “Off” status. | □ |
|  |  |  | Assess the corresponding status on the primary pump controller: “STATUS” LED is off. | □ |
| LEBT-010:VAC-VPT-99999_VT-00008 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. | Write down the value of the parameter before the modification: ________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : ________________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: ________________________________________ | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 138		LEBT-010:VAC-VPT-99999: “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-99999_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPT-99999_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VPT-99999_VT-00009 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-99999_VT-00010 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-99999_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-99999_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-99999_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the pump shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 139		LEBT-010:VAC-VPT-99999: “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPT-99999_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VPT-99999_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  |  |
| LEBT-010:VAC-VPT-99999_VT-00016 | Assess the on status of the pump. | Start the pump or assess the on status of the pump. | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-99999_VT-00017 | Verify that the tripped interlock stop the pump. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-99999_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-start the pump. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “On” status of the pump. | □ |
| LEBT-010:VAC-VPT-99999_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Off” status of the pump. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VPT-99999_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-start the pump. Re-establish the interlock according to the electrical diagram [6]. | Assess the “On” status of the pump. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VVA-99999

### Angle Valves & Gates Valves Verification: Support Environment.

See 4.1 for generic support environment.

### Angle Valves & Gates Valves Verification: Configuration

See 4.2 for generic configuration.

### Angle Valves & Gates Valves Verification: Setup

See 4.3 for generic setup.

Angle valve or gate valve shall be connected and shall not be open before starting the test.

A simulator can be used instead of the valve to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the valve.

The GUI panel shall show that the valve to be check is free of errors before starting the verification procedure.

### Angle Valves & Gates Valves Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the valve.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VVA-99999: List of requirements

| Reference to the requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VVA-07100_CR.01 | LEBT-010:VAC-VVA-07100_MR.01 | LEBT-010:VAC-VVA-07100_DAR.01 | LEBT-010:VAC-VVA-07100_CsR.01 | LEBT-010:VAC-VVA-07100_SR.01 | LEBT-010:VAC-VVA-07100_IR.01 |
| LEBT-010:VAC-VVA-07100_CR.02 | LEBT-010:VAC-VVA-07100_MR.02 | LEBT-010:VAC-VVA-07100_DAR.02 |  |  |  |
|  | LEBT-010:VAC-VVA-07100_MR.03 | LEBT-010:VAC-VVA-07100_DAR.03 |  |  |  |
|  | LEBT-010:VAC-VVA-07100_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VVA-07100_MR.05 |  |  |  |  |

#### LEBT-010:VAC-VVA-99999: Procedure of verification

LEBT-010:VAC-VVA-99999_VT-00001: Valve Cable Number __________________________________________(Check cable labelling on both side of the cable).

Table 140	LEBT-010:VAC-VVA-99999: Remote & Manual Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-99999_VT-00002 | Assess the closed status of the valve. | No action required because the valve shall already be closed. | Assess the “Close” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-99999_VT-00003 | Assess the “Undefined” status of the valve. | Disconnect the control cable from the connector on the valve. Wait that “Undefined” time-out elapsed. | Assess the “Undefined” status on the GUI panel. | □ |

Table 141	LEBT-010:VAC-VVA-99999: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-99999_VT-00004 | Verify the manual remote control of the valve. | Set “Manual” mode using the detailed GUI panel of the valve. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before opening the valve. | □ |
| LEBT-010:VAC-VVA-99999_VT-00005 | Verify the opening function. | Verify that there are no active interlocks applied to the valve. Open the valve through the GUI panel. | Assess the “Open” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-99999_VT-00006 | Verify the closing function. | Close the valve through the GUI panel. | Assess the “Close” status on the GUI panel. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 142	LEBT-010:VAC-VVA-99999: First “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-99999_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-99999_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VGP-00081 (Relay 3) _____________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-99999_VT-00009 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99999_VT-00010 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99999_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99999_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99999_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 143	LEBT-010:VAC-VVA-99999: Second “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-99999_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-99999_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-99999_VT-00016 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99999_VT-00017 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99999_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99999_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99999_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 144	LEBT-010:VAC-VVA-99999: First “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-99999_VT-00021 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-99999_VT-00022 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-99999_VT-00023 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99999_VT-00024 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99999_VT-00025 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99999_VT-00026 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99999_VT-00027 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 145	LEBT-010:VAC-VVA-99999: Second “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-99999_VT-00028 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-99999_VT-00029 | Interlock identification | Identify the source of the interlock (Device & Status): LEBT-010:VAC-VPT-99999 (Nominal Speed) _______________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-99999_VT-00030 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99999_VT-00031 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99999_VT-00032 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99999_VT-00033 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99999_VT-00034 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 146	LEBT-010:VAC-VVA-99999: Third “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-99999_VT-00035 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-99999_VT-00036 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-99999_VT-00037 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99999_VT-00038 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99999_VT-00039 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-99999_VT-00040 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-99999_VT-00041 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

## Test case LEBT-010:VAC-VGP-99999

### Gauge & Gauge Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Gauge & Gauge Controller Verification: Configuration

See 4.2 for generic configuration.

### Gauge & Gauge Controller Verification: Setup

See 4.3 for generic setup.

Gauge shall be under the nominal vacuum range before proceeding to the test.

Gauge shall be connected and shall not be measuring before starting the test.

Gauge controller shall be energized and shall not display any error to start the verification procedure.

A pre-calibrate simulator can be used instead of the gauge to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the gauge.

The GUI panel shall show that the gauge to be check is free of errors before starting the verification procedure.

### Gauge & Gauge Controller Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the gauge.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VGP-99999: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VGP-30000_CR.01 | LEBT-010:VAC-VGP-30000_MR.01 | LEBT-010:VAC-VGP-30000_DAR.01 | LEBT-010:VAC-VEG-10001_CsR.01 | LEBT-010:VAC-VEG-10001_SR.01 | LEBT-010:VAC-VEG-00011_IR.01 |
|  | LEBT-010:VAC-VGP-30000_MR.02 |  |  |  | LEBT-010:VAC-VEG-10001_IR.01 |
|  | LEBT-010:VAC-VGP-30000_MR.03 |  |  |  | LEBT-010:VAC-VEG-10010_IR.01 |
|  | LEBT-010:VAC-VGP-30000_MR.04 |  |  |  | LEBT-010:VAC-VEG-20020_IR.01 |
|  | LEBT-010:VAC-VGP-30000_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VGP-30000_MR.06 |  |  |  |  |
|  | LEBT-010:VAC-VGP-30000_MR.07 |  |  |  |  |
|  | LEBT-010:VAC-VGP-30000_MR.08 |  |  |  |  |
|  | LEBT-010:VAC-VGP-30000_MR.09 |  |  |  |  |
|  | LEBT-010:VAC-VGP-30000_MR.10 |  |  |  |  |
|  | LEBT-010:VAC-VGP-30000_MR.11 |  |  |  |  |

#### LEBT-010:VAC-VGP-99999: Procedure of verification

LEBT-010:VAC-VGP-99999_VT-00001: Gauge Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 147	LEBT-010:VAC-VGP-99999: Control & Monitoring (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGP-99999_VT-00002 | Assess the gauge “Off” status. | No action required because the gauge shall already be off. Off, the gauge shall display a pressure of 1000 mbar. | Assess the gauge “Off” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGP-99999_VT-00003 | Assess the gauge “On” status. | Stat the gauge. | Assess the “On” status of the gauge. | □ |
|  |  |  | Assess the “On” status of the gauge on the gauge controller. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGP-99999_VT-00004 | Verify the pressure archiving. | Open archiving appliance. | Assess the value of the archived pressure. | □ |
|  |  |  | Assess the consistency between the row value and the scaled value. | □ |
| LEBT-010:VAC-VGP-99999_VT-00005 | Verify the pressure archiving - Data Acquisition Alarm. | Disconnect or simulate a disconnection of the data acquisition analog measurement. | Assess the alarm on the control screen. | □ |

Table 148	LEBT-010:VAC-VGP-99999: Control & Monitoring (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGP-99999_VT-00006 | Verify the over-range status. | Create or simulate an over-range pressure to be read by the gauge. | Assess the gauge “Over-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGP-99999_VT-00007 | Verify the under-range status. | Create or simulate an under-range pressure to be read by the gauge. | Assess the gauge “Under-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGP-99999_VT-00008 | Verify that the parameters of the gauges can be remotely modified. | Choose a parameter relative to the gauge. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ____________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |
| LEBT-010:VAC-VGP-99999_VT-00009 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ___________ _________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |

## Test case LEBT-010:VAC-VGC-99999

### Gauge & Gauge Controller Verification: Support Environment.

See 4.1 for generic support environment.

### Gauge & Gauge Controller Verification: Configuration

See 4.2 for generic configuration.

### Gauge & Gauge Controller Verification: Setup

See 4.3 for generic setup.

Gauge shall be under the nominal vacuum range before proceeding to the test.

Gauge shall be connected and shall not be measuring before starting the test.

Gauge controller shall be energized and shall not display any error to start the verification procedure.

A pre-calibrate simulator can be used instead of the gauge to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the gauge.

The GUI panel shall show that the gauge to be check is free of errors before starting the verification procedure.

### Gauge & Gauge Controller Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the gauge.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VGC-99999: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VGC-30000_CR.01 | LEBT-010:VAC-VGC-30000_MR.01 | LEBT-010:VAC-VGC-30000_DAR.01 | LEBT-010:VAC-VEG-10001_CsR.01 | LEBT-010:VAC-VEG-10001_SR.01 | LEBT-010:VAC-VEG-00011_IR.01 |
|  | LEBT-010:VAC-VGC-30000_MR.02 |  |  |  | LEBT-010:VAC-VEG-10001_IR.01 |
|  | LEBT-010:VAC-VGC-30000_MR.03 |  |  |  | LEBT-010:VAC-VEG-10010_IR.01 |
|  | LEBT-010:VAC-VGC-30000_MR.04 |  |  |  | LEBT-010:VAC-VEG-20020_IR.01 |
|  | LEBT-010:VAC-VGC-30000_MR.05 |  |  |  |  |
|  | LEBT-010:VAC-VGC-30000_MR.06 |  |  |  |  |
|  | LEBT-010:VAC-VGC-30000_MR.07 |  |  |  |  |
|  | LEBT-010:VAC-VGC-30000_MR.08 |  |  |  |  |
|  | LEBT-010:VAC-VGC-30000_MR.09 |  |  |  |  |
|  | LEBT-010:VAC-VGC-30000_MR.10 |  |  |  |  |
|  | LEBT-010:VAC-VGC-30000_MR.11 |  |  |  |  |

#### LEBT-010:VAC-VGC-99999: Procedure of verification

LEBT-010:VAC-VGC-99999_VT-00001: Gauge Cable Number _________________________________________(Check cable labelling on both side of the cable).

Table 149	LEBT-010:VAC-VGC-99999: Control & Monitoring (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGC-99999_VT-00002 | Assess the gauge “Off” status. | No action required because the gauge shall already be off. Off, the gauge shall display a pressure of 1000 mbar. | Assess the gauge “Off” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGC-99999_VT-00003 | Assess the gauge “On” status. | Stat the gauge. | Assess the “On” status of the gauge. | □ |
|  |  |  | Assess the “On” status of the gauge on the gauge controller. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ________________________________________ | □ |
| LEBT-010:VAC-VGC-99999_VT-00004 | Verify the pressure archiving. | Open archiving appliance. | Assess the value of the archived pressure. | □ |
|  |  |  | Assess the consistency between the row value and the scaled value. | □ |
| LEBT-010:VAC-VGC-99999_VT-00005 | Verify the pressure archiving - Data Acquisition Alarm. | Disconnect or simulate a disconnection of the data acquisition analog measurement. | Assess the alarm on the control screen. | □ |

Table 150	LEBT-010:VAC-VGC-99999: Control & Monitoring (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VGC-99999_VT-00006 | Verify the over-range status. | Create or simulate an over-range pressure to be read by the gauge. | Assess the gauge “Over-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGC-99999_VT-00007 | Verify the under-range status. | Create or simulate an under-range pressure to be read by the gauge. | Assess the gauge “Under-Range” status. | □ |
|  |  |  | Write down the pressure displayed by the gauge: ____________________________________________ | □ |
| LEBT-010:VAC-VGC-99999_VT-00008 | Verify that the parameters of the gauges can be remotely modified. | Choose a parameter relative to the gauge. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ____________________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |
| LEBT-010:VAC-VGC-99999_VT-00009 | Verify that the parameters of the controller can be remotely modified. | Choose a parameter relative to the controller. Write down the Parameter: _____________________________________________. | Write down the value of the parameter before the modification: ___________ _________________________________ | □ |
|  |  | Modify the parameter. | Write down the value of the modified value of the parameter : __________________________________ | □ |
|  |  | Set the parameter to the desired value. | Write down the value of the parameter after the modification: _________________________________ | □ |

## Test case LEBT-010:VAC-VPG-20001

### Vacuum Pumping Group Verification: Support Environment.

See 4.1 for generic support environment.

### Vacuum Pumping Group Verification: Configuration

See 4.2 for generic configuration.

### Vacuum Pumping Group Verification: Setup

See 4.3 for generic setup.

Devices that constitute the pumping group shall be tested and verified beforehand.

Adjacent pumping group, LEBT-010:VAC-VPG-10001, connected to the first sector shall be stopped to proceed to all of these test.

The GUI panel shall show that the devices to be check are free of errors before starting the verification procedure.

### Vacuum Pumping Group Verification: Procedure

Remote commands shall be set and status shall be assessed using the detailed GUI panel of the device.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VPG-20001: List of requirements

| Reference to requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| No requirements | No requirements | No requirements | No requirements | LEBT-010:VAC-VEG-00011_SR.01 | No requirements |
|  |  |  |  | LEBT-010:VAC-VEG-00011_SR.02 |  |

#### LEBT-010:VAC-VPG-20001: Procedure of verification

Table 151	LEBT-010:VAC-VPG-20001: Pump-Down Atmospheric Pressure (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-20001_VT-00001 | Verify the pump down sequence (from atmospheric pressure). | Assess that the vacuum sector is at the atmospheric pressure. | Write down the actual pressure: _______________________________________ | □ |
|  |  | Set the “Normal” Mode. | Assess that it is not possible to start the pumping group. | □ |
|  |  |  | Assess the error. | □ |
|  |  | Disconnect the interlock from the gauge controller that conditions the starting of the turbomolecular pumps according to electrical diagram [6]. | Relay 5 of LEBT-010:VAC-VEG-00011 has been disconnected. | □ |
|  |  | Disconnect the open status of LEBT-010:VAC-VVA-00071 according to electrical diagram [6]. | Open status of LEBT-010:VAC-VVA-00071 is disconnected. | □ |
|  |  | Set the “Pump-Down” Mode. Reset the pumping group. | “Pump-Down” Mode is active. | □ |
|  |  |  | Assess that the error has disappeared. | □ |

Table 152	LEBT-010:VAC-VPG-20001: Pump-Down Atmospheric Pressure (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-20001_VT-00002 | Verify the pump down sequence (from atmospheric pressure). | Start the pumping group | Assess the opening of LEBT-010:VAC-VVA-00071. | □ |
|  |  |  | Assess the opening of LEBT-010:VAC-VVA-06100. | □ |
|  |  |  | Assess the opening of LEBT-010:VAC-VVA-07100. | □ |
|  |  |  | Assess the opening of LEBT-010:VAC-VVA-99998. | □ |
|  |  |  | Assess the opening of LEBT-010:VAC-VVA-99999. | □ |
|  |  |  | Assess the opening of ____-___:VAC-VVA-0__00. | □ |
|  |  |  | Assess the starting of the primary pump. | □ |
|  |  |  | Assess that turbomolecular pumps do not start. | □ |
|  |  | Wait that the delay has elapsed (more than 30s) | Assess that turbomolecular pumps do not start. | □ |
|  |  | Re-establish the interlock from the gauge controller that conditions the starting of the turbomolecular pumps according to electrical diagram [6]. | Assess that the turbomolecular pumps are starting. | □ |
|  |  | Pump down the vacuum sector. | Write down the pressure after having pumped down the sector: ___________________________ | □ |

Table 153	LEBT-010:VAC-VPG-20001: Normal Starting Sequence [sector under vacuum] (Part 1)

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-20001_VT-00003 | Verify the starting sequence (under vacuum). | Assess that the vacuum sector is under vacuum. | Write down the actual pressure: _______________________________________ | □ |
|  |  | Assess that the pumping group is stop. | All the pumps are off and the valves are close. | □ |
| LEBT-010:VAC-VPG-20001_VT-00004 | Disconnect the “interlocks” required by the sequences to progress (accordingly to the electrical diagram [6]). | Disconnect the interlock from the pump that conditions the opening of LEBT-010:VAC-VVA-00071. | Interlock has been disabled. | □ |
|  |  | Disconnect the interlock from the gauge controller that conditions the starting of the turbomolecular pumps. | Interlock has been disabled. | □ |
|  |  | Disconnect the interlock from the turbomolecular pump controller that conditions the opening of LEBT-010:VAC-VVA-06100. | Interlock has been disabled. | □ |
|  |  | Disconnect the interlock from the turbomolecular pump controller that conditions the opening of LEBT-010:VAC-VVA-07100. | Interlock has been disabled. | □ |
|  |  | Disconnect the interlock from the turbomolecular pump controller that conditions the opening of LEBT-010:VAC-VVA-99998. | Interlock has been disabled. | □ |
|  |  | Disconnect the interlock from the turbomolecular pump controller that conditions the opening of LEBT-010:VAC-VVA-99999. | Interlock has been disabled. | □ |
|  |  | Disconnect the interlock from the turbomolecular pump controller that conditions the opening of ____-___:VAC-VVA-0__00. | Interlock has been disabled. | □ |

Table 154	LEBT-010:VAC-VPG-20001: Normal Starting Sequence  [sector under vacuum] (Part 2)

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-20001_VT-00005 | Verify the starting sequence (under vacuum). | Start the pumping group. | Assess that the primary pump starts. | □ |
|  |  | Re-establish the interlock from the pump that conditions the opening of LEBT-010:VAC-VVA-00071. | Assess the opening of LEBT-010:VAC-VVA-00071. | □ |
|  |  | Re-establish disconnect the interlock from the gauge controller that conditions the starting of the turbomolecular pumps. | Assess the starting of the turbomolecular pumps. | □ |
|  |  | Once LEBT-010:VAC-VPT-06100 is at nominal speed, re-establish interlock from the turbomolecular pump controller that conditions the opening of LEBT-010:VAC-VVA-06100. | Assess the opening of LEBT-010:VAC-VVA-06100. | □ |
|  |  | Once LEBT-010:VAC-VPT-07100 is at nominal speed, re-establish interlock from the turbomolecular pump controller that conditions the opening of LEBT-010:VAC-VVA-07100. | Assess the opening of LEBT-010:VAC-VVA-07100. | □ |
|  |  | Once LEBT-010:VAC-VPT-99998 is at nominal speed, re-establish interlock from the turbomolecular pump controller that conditions the opening of LEBT-010:VAC-VVA-99998. | Assess the opening of LEBT-010:VAC-VVA-99998. | □ |
|  |  | OnceLEBT-010:VAC-VPT-99999 is at nominal speed, re-establish interlock from the turbomolecular pump controller that conditions the opening of LEBT-010:VAC-VVA-99999. | Assess the opening of LEBT-010:VAC-VVA-99999. | □ |
|  |  | Once ____-___:VAC-VPT-0__00 is at nominal speed, re-establish interlock from the turbomolecular pump controller that conditions the opening of ____-___:VAC-VVA-0__00. | Assess the opening of ____-___:VAC-VVA-0__00. | □ |

Table 155	LEBT-010:VAC-VPG-20001: Normal Stopping Sequence [sector under vacuum] (Part 1)

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-20001_VT-00006 | Verify the stopping sequence (under vacuum). | Assess that the vacuum sector is under vacuum. | Write down the actual pressure: _______________________________________ | □ |
|  |  | Assess that the pumping group is running. | All the pumps are running and all the valves are open. | □ |
| LEBT-010:VAC-VPG-20001_VT-00007 | Disconnect valves close status. | Disconnect the close status of ____-___:VAC-VVA-0__00 according to electrical diagram [6]. | Close status of ____-___:VAC-VVA-0__00 is disconnected. | □ |
|  |  | Disconnect the close status of LEBT-010:VAC-VVA-99999 according to electrical diagram [6]. | Close status of LEBT-010:VAC-VVA-99999 is disconnected. | □ |
|  |  | Disconnect the close status of LEBT-010:VAC-VVA-99998 according to electrical diagram [6]. | Close status of LEBT-010:VAC-VVA-99998 is disconnected. | □ |
|  |  | Disconnect the close status of LEBT-010:VAC-VVA-07100 according to electrical diagram [6]. | Close status of LEBT-010:VAC-VVA-07100 is disconnected. | □ |
|  |  | Disconnect the close status of LEBT-010:VAC-VVA-06100 according to electrical diagram [6]. | Close status of LEBT-010:VAC-VVA-06100 is disconnected. | □ |
|  |  | Disconnect the close status of LEBT-010:VAC-VVA-00071 according to electrical diagram [6]. | Close status of LEBT-010:VAC-VVA-00071 is disconnected. | □ |

Table 156	LEBT-010:VAC-VPG-20001: Normal Stopping Sequence [sector under vacuum] (Part 2)

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-20001_VT-00008 | Verify the stopping sequence (under vacuum). | Stop the pumping group. | Assess that the valves on the turbomolecular pumps are closed in the tunnel. | □ |
|  |  |  | Assess that the turbomolecular pumps are still running. | □ |

Table 157	LEBT-010:VAC-VPG-20001: Normal Stopping Sequence [sector under vacuum] (Part 3)

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-20001_VT-00009 | Reconnect valves close status. | Reconnect the close status of ____-___:VAC-VVA-0__00 according to electrical diagram [6]. | Assess the close status of ____-___:VAC-VVA-0__00. | □ |
|  |  |  | Assess that ____-___:VAC-VPT-0__00 is stopping. | □ |
|  |  | Reconnect the close status of LEBT-010:VAC-VVA-99999 according to electrical diagram [6]. | Assess the close status of LEBT-010:VAC-VVA-99999. | □ |
|  |  |  | Assess that LEBT-010:VAC-VPT-99999 is stopping. | □ |
|  |  | Reconnect the close status of LEBT-010:VAC-VVA-99998 according to electrical diagram [6]. | Assess the close status of LEBT-010:VAC-VVA-99998. | □ |
|  |  |  | Assess that LEBT-010:VAC-VPT-99998 is stopping. | □ |
|  |  | Reconnect the close status of LEBT-010:VAC-VVA-07100 according to electrical diagram [6]. | Assess the close status of LEBT-010:VAC-VVA-07100. | □ |
|  |  |  | Assess that LEBT-010:VAC-VPT-07100 is stopping. | □ |
|  |  | Reconnect the close status of LEBT-010:VAC-VVA-06100 according to electrical diagram [6]. | Assess the close status of LEBT-010:VAC-VVA-06100. | □ |
|  |  |  | Assess that LEBT-010:VAC-VPT-06100 is stopping. | □ |
|  |  | Reconnect the close status of LEBT-010:VAC-VVA-00071 according to electrical diagram [6]. | Assess the close status of LEBT-010:VAC-VVA-00071. | □ |
|  |  |  | Assess that LEBT-010:VAC-VPDP-00071 is stopping. | □ |

Table 158	LEBT-010:VAC-VPG-20001: Maintenance (Leak Detection) Sequence.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-20001_VT-00010 | Verify the leak detection sequence (under vacuum). | Assess that the vacuum sector is under vacuum. | Write down the actual pressure: _______________________________________ | □ |
|  |  | Assess that a leak detector is connected to the sector and is running. | Write down the actual pressure of the leak detector: _______________________________________ | □ |
|  |  | Assess that the pumping group is running and the turbomolecular pump is/are running at the nominal speed. | Pumps are running and valves are open. | □ |
|  |  | Switch to the “Leak Detection” Mode. | “Leak Detection” Mode is active. | □ |
|  |  | Manually open or close the valve upon the primary pump. | The valve upon the primary pump is manually controlled. | □ |
|  |  | Switch back to the “Normal” Mode. | “Leak Detection” Mode is active. | □ |
|  |  |  | The valve upon the primary pump is no more manually controlled. | □ |

Table 159	LEBT-010:VAC-VPG-20001: Local Protections (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-20001_VT-00011 | Assess the configuration of the hardware interlock. | Asses that the hardware interlock has been configured. | The interlock is not configured. | □ |
|  |  |  | The interlock is configured. | □ |
|  | Hardware interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
|  | Verify that the tripped interlock stop the pumping group. | Start the pumping group and wait that it reaches its nominal state. Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess that the group stop. | □ |
| LEBT-010:VAC-VPG-20001_VT-00012 | Assess the configuration of the software interlock. | Asses that the hardware interlock has been configured. | The interlock is not configured. | □ |
|  |  |  | The interlock is configured. | □ |
|  | Software interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
|  | Verify that the tripped interlock stop the pumping group. | Start the pumping group and wait that it reaches its nominal state. Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess that the group stop. | □ |

Table 160	LEBT-010:VAC-VPG-20001: Local Protections (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-20001_VT-00013 | Turbo-Pumps Controller Error | Start the pumping group and wait that it reaches its nominal state. Simulate an error on the first turbomolecular pump controller according to the electrical diagram [6]: LEBT-010:VAC-VEPT-06100. | Assess that the pumping group stops. | □ |
|  |  |  | Assess that the pumping group keep pumping. | □ |
|  |  | Do not reset the pumping group. Simulate an error on the second turbomolecular pump controller according to the electrical diagram [6] : LEBT-010:VAC-VEPT-07100. | Assess that the pumping group stop. | □ |
|  |  |  | Assess that the pumping group keep pumping. | □ |
|  |  | Do not reset the pumping group. Simulate an error on the third turbomolecular pump controller according to the electrical diagram [6] : LEBT-010:VAC-VEPT-99998. | Assess that the pumping group stops. | □ |
|  |  |  | Assess that the pumping group keep pumping. | □ |
|  |  | Do not reset the pumping group. Simulate an error on the fourth turbomolecular pump controller according to the electrical diagram [6] : LEBT-010:VAC-VEPT-99999. | Assess that the pumping group stops. | □ |
|  |  |  | Assess that the pumping group keep pumping. | □ |
|  |  | Do not reset the pumping group. Simulate an error on the fifth turbomolecular pump controller according to the electrical diagram [6] : ____-___:VAC-VEPT-_____. | Assess that the pumping group stops. | □ |
|  |  |  | Assess that the pumping group keep pumping. | □ |
|  |  | Re-establish each of the simulated errors. Reset the pumping group. | Assess that there are no errors on the pumping group. | □ |
|  |  |  | Assess that there is no error on any of the turbomolecular pump controllers. |  |

Table 161	LEBT-010:VAC-VPG-20001: Local Protections (Part 3).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-20001_VT-00014 | Power Supply Error | Start the pumping group and wait that it reaches its nominal state. Trigger or simulate a power supply error according to the electrical diagram [6]. | Assess that the pumping group stops. | □ |
|  | Power Supply Error - Automatic restart. | If the automatic restart function is used and has been set, re-establish the power supply or remove the simulation of the error. | Assess that the error message disappear. | □ |
|  |  |  | Assess that the pumping group is restarting. | □ |
| LEBT-010:VAC-VPG-20001_VT-00015 | Max Auto-Restart (If the automatic restart function is used and has been set) | Start the pumping group and wait that it reaches its nominal state. Trigger or simulate a power supply error according to the electrical diagram [6]. | Assess that the pumping group stops. | □ |
|  |  | Re-establish the power supply or remove the simulation of the error. | Assess that the error message disappear. | □ |
|  |  |  | Assess that the pumping group is restarting. | □ |
|  |  | Trigger or simulate a power supply error according to the electrical diagram [6]. | Assess that the pumping group stops. | □ |
|  |  | Wait that the maximal mount of restart tentative has been reached. Re-establish the power supply or remove the simulation of the error and do not reset the pumping group. | Assess that the pumping group doesn’t restart. | □ |

Table 162	LEBT-010:VAC-VPG-20001: Local Protections (Part 4 - Pressure Interlock).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-20001_VT-00016 | High Vacuum Manifold Vented Error- Pressure Interlock. | Identify the source of the interlock (Device & Relay) according to the settings document [7]: ____________________________________________________________________________________________ |  | □ |
|  |  | Write down the setting of the threshold before the test [7]:______________________________________________ |  | □ |
|  |  | Start the pumping group and wait that it reaches its nominal state. Set a new (unreachable) set-point or switch off the gauge or simulate that the relay has tripped. | Write down the threshold set for the test: _______________________________________ | □ |
|  |  |  | Assess that the pumping group stops. | □ |
|  | High Vacuum Manifold Vented Error- Pressure Interlock. Automatic restart. | If the automatic restart function is used and has been set, re-establish the setting of the threshold or remove the simulation of the error. | Assess that the error message disappear. | □ |
|  |  |  | Assess that the pumping group is restarting. | □ |
| LEBT-010:VAC-VPG-20001_VT-00017 | Low Vacuum Manifold Vented Error - Pressure Interlock. | Identify the source of the interlock (Device & Relay) according to the settings document [7]: LEBT-010:VAC-VGP-00081 (Relay 3) ______________________________________________________________ |  | □ |
|  |  | Write down the setting of the threshold before the test [7]:______________________________________________ |  | □ |
|  |  | Start the pumping group and wait that it reaches its nominal state. Set a new (unreachable) set-point or switch off the gauge or simulate that the relay has tripped. | Write down the threshold set for the test: _______________________________________ | □ |
|  |  |  | Assess that the pumping group stops. | □ |
|  | Low Vacuum Manifold Vented Error - Pressure Interlock Automatic restart. | If the automatic restart function is used and has been set, re-establish the setting of the threshold or remove the simulation of the error. | Assess that the error message disappear. | □ |
|  |  |  | Assess that the pumping group is restarting. | □ |

Table 163	LEBT-010:VAC-VPG-20001: Local Protections (Part 5 - Pressure Interlock).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-20001_VT-00018 | Vacuum Sector Vented - Pressure Interlock. | Pumping group stopped in normal mode. Vent the system at the atmospheric pressure. | Write down the threshold used to assess atmospheric pressure: _______________________________________ | □ |
|  |  |  | When the atmospheric pressure is reached, assess that the error appears. | □ |
|  |  | Pumping group stopped in normal mode. Sector vented at atmospheric pressure. Switch the operation mode to “Pump-Down” and reset the pumping group. | Assess that the error has disappeared. | □ |

Table 164	LEBT-010:VAC-VPG-20001: Local Protections (Part 6).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-20001_VT-00019 | Primary Pump Error Case 1: Pumping group without back-up primary pump. | Start the pumping group and wait that it reaches its nominal state. Trigger or simulate an error on the primary pump controller according to the electrical diagram [6]. | Assess that the pumping group stops. | □ |
|  | Primary Pump Error Case 2: Pumping group with back-up primary pump. | Start the pumping group and wait that it reaches its nominal state. Trigger or simulate an error on the primary pump controller according to the electrical diagram [6]. | Assess that the primary pump is stopped. | □ |
|  |  |  | Assess that the valve upon the primary pump is closes. | □ |
|  |  |  | Assess that the pumping group keeps running. | □ |
| LEBT-010:VAC-VPG-20001_VT-00020 | Primary Pump / Valve Error Case 1: Pumping group without back-up primary pump. | Pumping group stopped; disconnect the digital output that controls the valve upon the primary pump according to the electrical diagram [6]. Start the pumping group, wait that the error delay’s has elapsed. | Assess that the primary pump starts. | □ |
|  |  |  | Assess that the valve remain close. | □ |
|  |  |  | Assess that the pumping group stops after the delay. | □ |
|  | Primary Pump / Valve Error Case 2: Pumping group with back-up primary pump. | Pumping group stopped; lock close the valve upon the primary pump. Start the pumping group. | Assess that the primary pump starts. | □ |
|  |  |  | Assess that the valve remain close. | □ |
|  |  |  | Assess that the bypass valve open and that the pumping group keep starting. | □ |

Table 165	LEBT-010:VAC-VPG-20001: Local Protections (Part 7).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VPG-20001_VT-00021 | Turbo-Pumps Not Available | Pumping group stopped; lock off all the turbomolecular pumps controllers except one. | Only one turbomolecular pump controller has not been locked. | □ |
|  |  | Disconnect the digital input that read the nominal speed status of the non-locked turbomolecular pump controller according to the electrical diagram [6]. Start the pumping group. | Assess that the pumping group is starting. | □ |
|  |  | Once the turbomolecular pump controller has started, simulate an error. | Assess that the pumping group stops. | □ |

## Test case LEBT-010:VAC-VVA-00041

### Angle Valves & Gates Valves Verification: Support Environment.

See 4.1 for generic support environment.

### Angle Valves & Gates Valves Verification: Configuration

See 4.2 for generic configuration.

### Angle Valves & Gates Valves Verification: Setup

See 4.3 for generic setup.

Angle valve or gate valve shall be connected and shall not be open before starting the test.

A simulator can be used instead of the valve to proceed to these tests beforehand. In case of use of a simulator, tests cannot be validated with the simulator and must be performed using the valve.

The GUI panel shall show that the valve to be check is free of errors before starting the verification procedure.

### Angle Valves & Gates Valves Verification: Procedure

Commands shall be set and status shall be assessed using the detailed GUI panel of the valve.

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-VVA-00041: List of requirements

| Reference to the requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| LEBT-010:VAC-VVA-00041_CR.01 | LEBT-010:VAC-VVA-00041_MR.01 | LEBT-010:VAC-VVA-00041_DAR.01 | LEBT-010:VAC-VVA-00041_CsR.01 | LEBT-010:VAC-VVA-00041_SR.01 | LEBT-010:VAC-VVA-00041_IR.01 |
| LEBT-010:VAC-VVA-00041_CR.02 | LEBT-010:VAC-VVA-00041_MR.02 | LEBT-010:VAC-VVA-00041_DAR.02 |  |  |  |
|  | LEBT-010:VAC-VVA-00041_MR.03 | LEBT-010:VAC-VVA-00041_DAR.03 |  |  |  |
|  | LEBT-010:VAC-VVA-00041_MR.04 |  |  |  |  |
|  | LEBT-010:VAC-VVA-00041_MR.05 |  |  |  |  |

#### LEBT-010:VAC-VVA-00041: Procedure of verification

LEBT-010:VAC-VVA-00041_VT-00001: Pump Cable Number __________________________________________(Check cable labelling on both side of the cable).

Table 166	LEBT-010:VAC-VVA-00041: Remote & Manual Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00041_VT-00002 | Assess the closed status of the valve. | No action required because the valve shall already be closed. | Assess the “Close” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-00041_VT-00003 | Assess the “Undefined” status of the valve. | Disconnect the control cable from the connector on the valve. Wait that “Undefined” time-out elapsed. | Assess the “Undefined” status on the GUI panel. | □ |

Table 167	LEBT-010:VAC-VVA-00041: Remote Control (Part 2).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00041_VT-00004 | Verify the manual remote control of the valve. | Set “Manual” mode using the detailed GUI panel of the valve. | Assess the “Manual” status on the GUI panel. | □ |
|  |  |  | Make sure that the system is in a safe condition before opening the valve. | □ |
| LEBT-010:VAC-VVA-00041_VT-00005 | Verify the opening function. | Verify that there are no active interlocks applied to the valve. Open the valve through the GUI panel. | Assess the “Open” status on the GUI panel. | □ |
| LEBT-010:VAC-VVA-00041_VT-00006 | Verify the closing function. | Close the valve through the GUI panel. | Assess the “Close” status on the GUI panel. | □ |

Table 168	LEBT-010:VAC-VVA-00041: Automatic Control (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00041_VT-00042 | Verify the automatic opening of the valve. | Start both pumping groups and wait that have reached their nominal state. | Assess that the valve remain closed. | □ |
|  |  | Trigger an error on the primary pump controller or simulate it according to the electrical diagram [6]. | Assess that the valve is open. | □ |
|  |  |  | Assess that both pumping groups are still running. | □ |
| LEBT-010:VAC-VVA-00041_VT-00043 | Verify the automatic closure of the valve. | Stop both pumping groups. | Assess that the two pumping groups stop. | □ |
|  |  |  | Assess that the valve closes. | □ |
| LEBT-010:VAC-VVA-00041_VT-00044 | Verify the automatic opening of the valve. | Lock off the faulty pump. Reset the pumping groups. | Assess that the two pumping groups are starting. | □ |
|  |  |  | Assess that the valve is open. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 169		LEBT-010:VAC-VVA-00041: First “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00041_VT-00007 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-00041_VT-00008 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-00041_VT-00009 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00041_VT-00010 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00041_VT-00011 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00041_VT-00012 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00041_VT-00013 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 170		LEBT-010:VAC-VVA-00041: Second “Pressure” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00041_VT-00014 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-00041_VT-00015 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-00041_VT-00016 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00041_VT-00017 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00041_VT-00018 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00041_VT-00019 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00041_VT-00020 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 171	LEBT-010:VAC-VVA-00041: First “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00041_VT-00021 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-00041_VT-00022 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-00041_VT-00023 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00041_VT-00024 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00041_VT-00025 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00041_VT-00026 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00041_VT-00027 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 172	LEBT-010:VAC-VVA-00041: Second “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00041_VT-00028 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-00041_VT-00029 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-00041_VT-00030 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00041_VT-00031 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00041_VT-00032 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00041_VT-00033 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00041_VT-00034 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

| Specific setup: | To perform these tests, the valve shall be safely operated regarding to the vacuum conditions, the source of the interlock shall be tested beforehand. |
| --- | --- |

Table 173	LEBT-010:VAC-VVA-00041: Third “Hardware” Interlock.

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-VVA-00041_VT-00035 | Assess the configuration of the interlock. | Asses that the interlock has been configured. | The interlock is configured. | □ |
|  |  |  | The interlock is not configured. | □ |
| LEBT-010:VAC-VVA-00041_VT-00036 | Interlock identification | Identify the source of the interlock (Device & Status): _________________________________________________________________________________________ |  | □ |
| LEBT-010:VAC-VVA-00041_VT-00037 | Assess the open status of the valve. | Open the valve or assess the open status of the valve. | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00041_VT-00038 | Verify that the tripped interlock close the valve. | Trigger the interlock or simulate it according to the electrical diagram [6]. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00041_VT-00039 | Verify the bypass of a tripped interlock. | Override the interlock and reset the interlock fault. Re-open the valve. | Assess the override status of the interlock. | □ |
|  |  |  | Assess the “Open” status of the valve. | □ |
| LEBT-010:VAC-VVA-00041_VT-00040 | Verify the clear bypass function (the reactivation of the interlocks). | Clear the bypass command. | Assess the “Close” status of the valve. | □ |
|  |  |  | Assess the tripped status of the interlock. | □ |
| LEBT-010:VAC-VVA-00041_VT-00041 | Verify the automatic activation of the interlock. | Override the interlock, reset the interlock fault and re-open the valve. Re-establish the interlock according to the electrical diagram [6]. | Assess the “Open” status of the valve. | □ |
|  |  |  | Assess the healthy status of the interlock. | □ |

# Test Cases “:VAC-PLCIO-" (PLC tests)

## Test case LEBT-010:VAC-PLCIO-10001

### PLC Remote I/Os Verification: Support Environment.

See 4.1 for generic support environment.

### PLC Remote I/Os Verification: Configuration

See 4.2 for generic configuration.

### PLC Remote I/Os Verification: Setup

See 4.3 for generic setup.

All vacuum devices shall be stopped before starting the following tests.

### PLC Remote I/Os Verification: Procedure

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-PLCIO-10001: List of requirements

| Reference to the requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| No requirements | No requirements | No requirements | No requirements | No requirements | No requirements |

#### LEBT-010:VAC-PLCIO-10001: Procedure of verification

LEBT-010:VAC-PLCIO-10001: Network Cable Number __________________________________________(Check cable labelling on both side of the cable).

Table 174		LEBT-010:VAC-PLCIO-10001: Hardware Fault Detection (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-PLCIO-10001_VT-00002 | PLC hardware fault detection. | Trigger a PLC hardware error on the remote I/O station. | Assess the error on the GUI panel. | □ |
|  |  |  | Assess the invalid status. | □ |

## Test case LEBT-010:VAC-PLCIO-01001

### PLC Remote I/Os Verification: Support Environment.

See 4.1 for generic support environment.

### PLC Remote I/Os Verification: Configuration

See 4.2 for generic configuration.

### PLC Remote I/Os Verification: Setup

See 4.3 for generic setup.

All vacuum devices shall be stopped before starting the following tests.

### PLC Remote I/Os Verification: Procedure

The tables bellow list requirements to be fulfilled and tests to be achieved.

#### LEBT-010:VAC-PLCIO-01001: List of requirements

| Reference to the requirements [4] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Control Requirements | Monitoring and Graphical User Interface Requirements | Data Acquisition and Archiving Requirements | Constraint Requirements | Conventional Safety Requirements | Interface Requirements |
| No requirements | No requirements | No requirements | No requirements | No requirements | No requirements |

#### LEBT-010:VAC-PLCIO-01001: Procedure of verification

LEBT-010:VAC-PLCIO-01001: Network Cable Number __________________________________________(Check cable labelling on both side of the cable).

Table 175		LEBT-010:VAC-PLCIO-01001: Hardware Fault Detection (Part 1).

| Verification Plan ID | Verification Description | Action | Pass Criteria Statement | Verification is valid (tick box) |
| --- | --- | --- | --- | --- |
| LEBT-010:VAC-PLCIO-01001_VT-00002 | PLC hardware fault detection. | Trigger a PLC hardware error on the remote I/O station. | Assess the error on the GUI panel. | □ |
|  |  |  | Assess the invalid status. | □ |

# Glossary

| Term | Definition |
| --- | --- |
| CPU | Central Processing Unit |
| EPICS | Experimental Physics and Industrial Control System |
| FB | Function Block - Siemens function type |
| FBS | Functional Breakdown Structure |
| ICS | Integrated Control System |
| LBS | Location Breakdown Structure |
| LINAC | Linear Accelerator |
| OPI | Operator Interface |
| PLC | Programmable Logical Controller |

# references

- Proton Beam Vacuum Control System
System Engineering Management Plan (ESS-0090062)

- Proton Beam Vacuum Interlock System
System Engineering Management Plan (ESS-0087015)

- LEBT Vacuum Control Systems
System Engineering Management Plan (ESS-0087029)

- LEBT Vacuum Control Systems
System Requirement Specification (ESS-0087031)

- Vacuum Symbols and ICS Naming (ESS-0043149)

- Accelerator Vacuum Controls
Wiring diagrams vacuum control racks (ESS-0092887)

- Controller Setpoints (ESS-0217939)

- ISRC + LEBT Vacuum Diagram (ESS-0085792)

- Decision summary for ESS naming, tagging and structuring of data (ESS-0036752).

- ESS Guideline for ESS Breakdown Structures (ESS-048668)

- Naming Service: https://naming.esss.lu.se/

- Control Configuration Data Base: https://ccdb.esss.lu.se/

- ics_plc_factory: https://bitbucket.org/europeanspallationsource/ics_plc_factory

- S7-SCL: simatic-s7-scl

- ESS Guideline for PLC Code Development (ESS-0058761)

- Bitbucket: https://bitbucket.org/europeanspallationsource/

- Bitbucket - EPICS PLC Interface Project: https://bitbucket.org/account/user/europeanspallationsource/projects/EPI

- Bitbucket - EPICS PLC Interface - Definition File: 
https://bitbucket.org/europeanspallationsource/linac-vac-vpp_vac-vpdp/src

- ESS IOC Factory: https://iocfactory.esss.lu.se/

- Proton Beam Vacuum Control System - Control system Integration (ESS-0158136)

Changes summary

| Revision | Description of the changes |
| --- | --- |
| 1 | First issue |
| 2 | -LEBT-010:VAC-IOC-11010 replaced by VacS-ACCV:VAC-IOC11010. -Update of the name of the PLC Project. |

Document Revision history

| Revision | Reason for and description of change | Author | Date |
| --- | --- | --- | --- |
| 1 | First issue | François Bellorini | 2018-01-19 |